## Line_data_20181231
These data are giving the situation on the internal equipment as of 20181231
Substation 1 | Substation 1 - Full name | Substation 2 | Substation 2 - Full name | U | U/Nr. | Length | Inom | R | X | ωC
[5 empty] | (kV) | (Km) | (A) | (Ω) | (Ω) | (μS)
ACHEN | ACHENE | GRAMM | GRAMME | 380 | 380 / 10 | 36.9 | 1999 | 1.14 | 12.1 | 141.47
ACHEN | ACHENE | ACHES | ACHENE SNCB | 380 | 380 / 200 | 0.1 | 2186 | 0.01 | 0.14 | 0
ANDUM | ANDRE DUMONT | ZUTE+ | ZUTENDAAL | 380 | 380 / 12 | 6.3 | 2000 | 0.21 | 1.98 | 22.97
AUBAN | AUBANGE | BRUME | BRUME | 380 | 380 / 13 | 104.4 | 2186 | 3.55 | 32.88 | 379.36
AVLGM | AVELGEM | HORTA | HORTA | 380 | 380 / 101 | 39.7 | 1999 | 1.23 | 13.02 | 146.89
AVLGM | AVELGEM | HORTA | HORTA | 380 | 380 / 102 | 39.7 | 2186 | 1.25 | 13 | 152.96
AVLGM | AVELGEM | IZGEM | IZEGEM | 380 | 380 / 46 | 22.8 | 2186 | 0.71 | 7.48 | 87.65
AVLGM | AVELGEM | IZGEM | IZEGEM | 380 | 380 / 47 | 22.8 | 2186 | 0.71 | 7.48 | 87.65
BRUEG | BRUEGEL | MEKI+ | MEKINGEN | 380 | 380 / 33 | 14 | 1999 | 0.45 | 4.63 | 54.18
BRUEG | BRUEGEL | COURC | COURCELLES | 380 | 380 / 34 | 47.3 | 2186 | 1.47 | 15.51 | 182.6
BRUEG | BRUEGEL | BUGG+ | BUGGENHOUT | 380 | 380 / 35 | 15.9 | 1999 | 0.61 | 5.11 | 59.8
BRUEG | BRUEGEL | BUGG+ | BUGGENHOUT | 380 | 380 / 36 | 15.9 | 2186 | 0.5 | 5.25 | 61.8
BRUME | BRUME | GRAMM | GRAMME | 380 | 380 / 1 | 44.3 | 1999 | 1.37 | 14.53 | 164
BRUME | BRUME | GRAMM | GRAMME | 380 | 380 / 2 | 44.3 | 2322 | 1.37 | 14.53 | 170.38
BRUME | BRUME | COO | COO | 380 | 380 / 3 | 2 | 1999 | 0.06 | 0.66 | 7.72
BRUME | BRUME | COO | COO | 380 | 380 / 4 | 2 | 1999 | 0.06 | 0.66 | 7.72
BUGG+ | BUGGENHOUT | MERCA | MERCATOR | 380 | 380 / 35 | 15.5 | 1999 | 0.59 | 5 | 58.6
BUGG+ | BUGGENHOUT | VERBR | VERBRANDE BRUG | 380 | 380 / 35 | 21.7 | 2319 | 0.66 | 6.91 | 83.46
BUGG+ | BUGGENHOUT | MERCA | MERCATOR | 380 | 380 / 36 | 15.5 | 2186 | 0.48 | 5.08 | 58.8
BUGG+ | BUGGENHOUT | VERBR | VERBRANDE BRUG | 380 | 380 / 36 | 21.7 | 2186 | 0.67 | 7.12 | 83.46
CHAMP | CHAMPION (NAMUR) | GRAMM | GRAMME | 380 | 380 / 32 | 32.2 | 2186 | 1 | 10.56 | 124.25
CHAMP | CHAMPION (NAMUR) | COURC | COURCELLES | 380 | 380 / 56 | 44.1 | 2186 | 1.37 | 14.46 | 170.24
COURC | COURCELLES | STAM+ | ST-AMAND | 380 | 380 / 31 | 12.6 | 1999 | 0.39 | 4.13 | 48.64
COURC | COURCELLES | MEKI+ | MEKINGEN | 380 | 380 / 33 | 33.4 | 1999 | 1.03 | 10.95 | 128.2
COURC | COURCELLES | GOUY | GOUY | 380 | 380 / 57 | 1.7 | 1999 | 0.05 | 0.56 | 6.6
COURC | COURCELLES | GOUY | GOUY | 380 | 380 / 58 | 1.8 | 2186 | 0.06 | 0.59 | 7
DOEL | DOEL | ZANDV | ZANDVLIET | 380 | 380 / 25 | 6.8 | 1999 | 0.24 | 2.4 | 24
DOEL | DOEL | ZANDV | ZANDVLIET | 380 | 380 / 26 | 7.1 | 1999 | 0.07 | 2.57 | 22.92
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 51 | 22.8 | 1999 | 0.71 | 7.48 | 88
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 52 | 22.8 | 1999 | 0.71 | 7.48 | 88
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 53 | 22.2 | 2186 | 0.8 | 6.84 | 80
DOEL | DOEL | MERCA | MERCATOR | 380 | 380 / 54 | 22.2 | 2186 | 0.8 | 6.84 | 80
DROGE | DROGENBOS | MEKI+ | MEKINGEN | 380 | 380 / 33 | 10.3 | 2186 | 0.32 | 3.38 | 39.61
EEKLN | EEKLO NOORD | HORTA | HORTA | 380 | 380 / 103 | 13 | 4560 | 0.4 | 4.26 | 50.27
EEKLN | EEKLO NOORD | MAERL | VAN MAERLANT | 380 | 380 / 103 | 17.3 | 4689 | 0.28 | 4.07 | 79.6
GEZEL | GEZELLE | MAERL | VAN MAERLANT | 380 | 380 / 107 | 10.1 | 1635 | 0.09 | 2.24 | 725.81
GEZEL | GEZELLE | MAERL | VAN MAERLANT | 380 | 380 / 108 | 10.1 | 1635 | 0.09 | 2.23 | 725.81
GEZEL | GEZELLE | MAERL | VAN MAERLANT | 380 | 380 / 109 | 10.1 | 1635 | 0.11 | 2.21 | 725.81
GEZEL | GEZELLE | MAERL | VAN MAERLANT | 380 | 380 / 110 | 10.1 | 1635 | 0.11 | 2.21 | 725.81
GEZEL | GEZELLE | STEVN | STEVIN | 380 | 380 / 111 | 8 | 4644 | 0.13 | 1.9 | 18.42
GEZEL | GEZELLE | STEVN | STEVIN | 380 | 380 / 112 | 8 | 4644 | 0.13 | 1.9 | 18.42
GEZEL | GEZELLE | NEMO | NEMO | 380 | 380 / 114 | 0.8 | 1635 | 0.01 | 0.07 | 56.19
GRAMM | GRAMME | LIXHE | LIXHE | 380 | 380 / 11 | 53.4 | 2051 | 3.04 | 20.03 | 170.88
GRAMM | GRAMME | ZUTE+ | ZUTENDAAL | 380 | 380 / 12 | 55.6 | 2000 | 1.85 | 17.45 | 202.7
GRAMM | GRAMME | TIHA2 | TIHANGE 2 | 380 | 380 / 17 | 2.6 | 2186 | 0.08 | 0.85 | 10.04
GRAMM | GRAMME | TIHA3 | TIHANGE 3 | 380 | 380 / 18 | 3.3 | 2186 | 0.1 | 1.08 | 12.74
GRAMM | GRAMME | STAM+ | ST-AMAND | 380 | 380 / 31 | 56.4 | 1999 | 1.75 | 18.5 | 217.8
GRAMM | GRAMME | TIHA1 | TIHANGE 1 | 380 | 380 / 5 | 2.9 | 1999 | 0.09 | 0.95 | 11.19
GRAMM | GRAMME | TIHA1 | TIHANGE 1 | 380 | 380 / 6 | 2.9 | 1999 | 0.09 | 0.95 | 11.19
GRAMM | GRAMME | RIMIE | RIMIERE | 380 | 380 / 7 | 14.6 | 1999 | 0.45 | 4.79 | 54
HORTA | HORTA | MAERL | VAN MAERLANT | 380 | 380 / 104 | 29 | 4689 | 0.43 | 7.94 | 115.83
HORTA | HORTA | MERCA | MERCATOR | 380 | 380 / 73 | 48.4 | 3400 | 1.58 | 15.19 | 176.33
HORTA | HORTA | RODE+ | RODENHUIZE | 380 | 380 / 74 | 14.2 | 2186 | 0.44 | 4.64 | 54.71
LINT | LINT | MERCA | MERCATOR | 380 | 380 / 59 | 21.1 | 2186 | 0.65 | 6.92 | 73.8
LINT | LINT | MASSE | MASSENHOVEN | 380 | 380 / 61 | 14.1 | 2188 | 0.46 | 4.56 | 50.17
LINT | LINT | MERCA | MERCATOR | 380 | 380 / 61 | 21.1 | 2186 | 0.65 | 6.92 | 73.8
LIXHE | LIXHE | VANYK | VAN EYCK | 380 | 380 / 91 | 53 | 1999 | 2.07 | 16.53 | 192.96
MASSE | MASSENHOVEN | MEERH | MEERHOUT | 380 | 380 / 21 | 32.5 | 2186 | 1.01 | 10.66 | 125.4
MASSE | MASSENHOVEN | MERCA | MERCATOR | 380 | 380 / 60 | 35 | 2186 | 1.09 | 11.54 | 123.2
MEERH | MEERHOUT | VANYK | VAN EYCK | 380 | 380 / 23 | 57.5 | 2186 | 1.78 | 18.86 | 220.86
MERCA | MERCATOR | RODE+ | RODENHUIZE | 380 | 380 / 74 | 34.2 | 1999 | 1.07 | 11.21 | 132.2
RODE+ | RODENHUIZE | RODEN | RODENHUIZE | 380 | 380 / 74 | 0.2 | 2186 | 0.01 | 0.14 | 0
STAM+ | ST-AMAND | TERGN | TERGNEE | 380 | 380 / 31 | 7.5 | 2186 | 0.23 | 2.46 | 27.76
TIBIS | TIHANGE BIS | TIHA2 | TIHANGE 2 | 380 | 380 / 15 | 1 | 2322 | 0.03 | 0.31 | 3.8
VANYK | VAN EYCK | ZUTE+ | ZUTENDAAL | 380 | 380 / 12 | 31.1 | 1999 | 0.72 | 9.55 | 114.35
AUBAN | AUBANGE | VILLE | VILLEROUX | 220 | 220 / 506 | 47.2 | 1063 | 4.01 | 14.16 | 154.16
AUBAN | AUBANGE | HEINS | HEINSCH | 220 | 220 / 507 | 15 | 1063 | 1.6 | 4.41 | 48.98
AUBAN | AUBANGE | LATO+ | LATOUR | 220 | 220 / 515 | 15.5 | 890 | 1.19 | 6.17 | 43.4
AUBAN | AUBANGE | SMARD | ST-MARD | 220 | 220 / 516 | 21.1 | 890 | 1.62 | 8.4 | 59
AWIRS | AWIRS | LEVAL | LE VAL | 220 | 220 / 521 | 6.6 | 1092 | 0.33 | 2.64 | 18.65
AWIRS | AWIRS | RIMIE | RIMIERE | 220 | 220 / 535 | 7.4 | 976 | 0.47 | 3.13 | 20.06
BRUME | BRUME | HOUF+ | HOUFFALIZE | 220 | 220 / 504 | 27.5 | 1244 | 1.62 | 8.14 | 96.24
HOUF+ | HOUFFALIZE | HOUFF | HOUFFALIZE | 220 | 220 / 504 | 0.3 | 1244 | 0.02 | 0.09 | 1.06
JUPIL | JUPILLE | RIMIE | RIMIERE | 220 | 220 / 538 | 20.2 | 1092 | 0.61 | 4.52 | 57.64
LATO+ | LATOUR | LATOU | LATOUR | 220 | 220 / 515 | 0.2 | 890 | 0.02 | 0.08 | 0.56
LATO+ | LATOUR | SMARD | ST-MARD | 220 | 220 / 515 | 5.6 | 890 | 0.43 | 2.22 | 15.68
LATRO | LA TROQUE | SERAI | SERAING | 220 | 220 / 524 | 2.5 | 1050 | 0.15 | 1.01 | 7.03
LATRO | LA TROQUE | SERAI | SERAING | 220 | 220 / 525 | 2.5 | 1050 | 0.15 | 1.01 | 7.03
LEVAL | LE VAL | RIMIE | RIMIERE | 220 | 220 / 522 | 13.4 | 976 | 0.77 | 5.29 | 37.4
LEVAL | LE VAL | SERAI | SERAING | 220 | 220 / 523 | 2.9 | 1037 | 0.17 | 1.17 | 8.2
MARC+ | MARCOURT | MARCO | MARCOURT | 220 | 220 / 501 | 0.6 | 1063 | 0.05 | 0.18 | 1.96
MARC+ | MARCOURT | RIMIE | RIMIERE | 220 | 220 / 501 | 38 | 1063 | 3.23 | 11.3 | 124.11
MARC+ | MARCOURT | SENO+ | SENONCHAMPS | 220 | 220 / 501 | 26.8 | 1063 | 2.28 | 8.04 | 87.52
OS2ST | OFFSHORE ON STEVIN | STEVN | STEVIN | 220 | 220 / 4 | 40.9 | 1001 | 1.99 | 4.57 | 2884.34
RIMIE | RIMIERE | SERAI | SERAING | 220 | 220 / 533 | 11.4 | 1037 | 0.66 | 4.63 | 31.8
ROMSE | ROMSEE | SERAI | SERAING | 220 | 220 / 530 | 14.3 | 1037 | 0.83 | 5.81 | 40.2
ROMSE | ROMSEE | ROMSS | ROMSEE SNCB | 220 | 220 / 536 | 1 | 10000 | 0 | 0.05 | 0
ROMSE | ROMSEE | ROMSS | ROMSEE SNCB | 220 | 220 / 537 | 1 | 1177 | 0 | 0.05 | 0
ROUVR | ROUVROY | SMARD | ST-MARD | 220 | 220 / 518 | 0.7 | 890 | 0.05 | 0.28 | 2
SENO+ | SENONCHAMPS | VILLE | VILLEROUX | 220 | 220 / 501 | 2.6 | 1063 | 0.63 | 2.15 | 8.49
SMARD | ST-MARD | SMARS | ST-MARD SNCB | 220 | 220 / 601 | 1 | 10000 | 0 | 0.05 | 0
SMARD | ST-MARD | SMARS | ST-MARD SNCB | 220 | 220 / 602 | 1 | 10000 | 0 | 0.05 | 0
STEVN | STEVIN | ZNAAM | BANK ZONDER NAAM | 220 | 220 / 1 | 45.4 | 1005 | 1.77 | 5.55 | 2699.13

## Interconnections_data_20181231
These data are coming from the ENTSO-e reference case, situation as of 2081231. X-node is in the electrical middle of the line.
These data will be updated when ENTSO-e reference case is updated.
Substation 1 | Substation 1 - Full name | X-node | Substation 2 - Full name | U | U/Nr. | Length | Inom | R | X | ωC
[5 empty] | (kV) | (km) | (A) | (Ω) | (Ω) | (μS)
MONCE | MONCEAU | XMO_CH21 | CHOOZ | 220 | 220 / 48 | 29.4 | 1058 | 1.66 | 5.86 | 38.24
AUBAN | AUBANGE | ESCH | ESCH / BELVAL | 220 | 220 / 511 | 1 | 1037 | 0.88 | 6.17 | 42.98
AUBAN | AUBANGE | XAU_SA21 | SANEM | 220 | 220 / 512 | 5.8 | 1037 | 0.33 | 1.17 | 8.09
AUBAN | AUBANGE | XAU_MO22 | MOULAINE | 220 | 220 / 513 | 7.8 | 1160 | 0.44 | 3.48 | 13.71
AUBAN | AUBANGE | XAU_M.21 | MOULAINE | 220 | 220 / 514 | 1.9 | 1160 | 0.11 | 0.81 | 6.26
ACHEN | ACHENE | XAC_LO11 | LONNY | 380 | 380 / 19 | 31.5 | 1999 | 0.78 | 9.54 | 94.12
VANYK | VAN EYCK | XVY_MB12 | MAASBRACHT | 380 | 380 / 27 | 5.5 | 2186 | 0.14 | 1.58 | 22.88
VANYK | VAN EYCK | XVY_MB11 | MAASBRACHT | 380 | 380 / 28 | 5.5 | 1999 | 0.14 | 1.58 | 22.96
ZANDV | ZANDVLIET | XZA_BS11 | BORSSELE | 380 | 380 / 29 | 23.7 | 2499 | 0.58 | 6.53 | 98.41
ZANDV | ZANDVLIET | XZA_GT11 | GEERTRUIDENBERG | 380 | 380 / 30 | 33.5 | 2499 | 0.82 | 9.23 | 139.06
AVLGM | AVELGEM | XAV_MA11 | MASTAING | 380 | 380 / 79 | 38.5 | 1999 | 0.95 | 11.48 | 95.55
AVLGM | AVELGEM | XAV_AV11 | AVELIN | 380 | 380 / 80 | 21.4 | 2322 | 0.57 | 6.58 | 77.31

## Transformer_data_20181231
These data are giving the situation on the internal equipment as of 20181231.
PUTM | Substation | Substation - Full name | U / Expl.Nr | V1 | V2 | V3 | Pnom1 | Pnom2 | Pnom3 | Zcc12 | Zcc13 | Zcc23 | Min Tap | Nom Tap | Max Tap | ∆V /tap
|  |  |  | (kV) | (kV) | (kV) | (MVA) | (MVA) | (MVA) | (%) | (%) | (%) | # | # | # | (%Unom)
ACHEN380 T 1 380/ 70/36 TFO ¦ | ACHEN | ACHENE | 380 / T 1 | 400 | 76 | 36 | 220 | 220 | 50 | 20.7 | 6.9 | 12.1 | 1 | 18 | 35 | -0.88
AUBAN220 T 9 220/ 70/15 TFO ¦ | AUBAN | AUBANGE | 220 / T 9 | 222 | 74 | 17 | 90 | 90 | 30 | 12.8 | 7.1 | 13.3 | 1 | 12 | 23 | 1.64
AUBAN380 T 1 380/220/36 TFO ¦ | AUBAN | AUBANGE | 380 / T 1 | 400 | 245 | 36 | 300 | 300 | 15 | 15.4 | 5.4 | 7 | 1 | 11 | 24 | 0.87
AUBAN380 T 2 380/220/36 TFO ¦ | AUBAN | AUBANGE | 380 / T 2 | 400 | 245 | 36 | 300 | 300 | 15 | 15.1 | 4.6 | 6.1 | 1 | 11 | 24 | 0.86
AVLGM380 T 1 380/150/36 TFO ¦ | AVLGM | AVELGEM | 380 / T 1 | 400 | 165 | 34 | 450 | 450 | 15 | 17.9 | 1.2 | 2.2 | 1 | 12 | 24 | 1.01
AVLGM380 T 2 380/150/36 TFO ¦ | AVLGM | AVELGEM | 380 / T 2 | 400 | 165 | 34 | 555 | 555 | 15 | 22.4 | 1.1 | 2 | 1 | 12 | 24 | 1
AWIRS220 T 7 220/150/15 TFO ¦ | AWIRS | AWIRS | 220 / T 7 | 225 | 145 | 16 | 375 | 375 | 25 | 14.1 | 6.9 | 8.9 | 1 | 7 | 21 | 0.71
AWIRS220 T 8 220/ 70/70 TFO ¦ | AWIRS | AWIRS | 220 / T 8 | 225 | 72 | 72 | 160 | 80 | 80 | 14.9 | 27.6 | 14.8 | 1 | 7 | 19 | -1.25
BRUEG380 T 1 380/150/36 TFO ¦ | BRUEG | BRUEGEL | 380 / T 1 | 400 | 165 | 36 | 555 | 555 | 75 | 22.2 | 10.2 | 6.5 | 1 | 12 | 24 | 0.92
BRUEG380 T 2 380/150/36 TFO ¦ | BRUEG | BRUEGEL | 380 / T 2 | 400 | 165 | 36 | 555 | 555 | 75 | 22.2 | 10.2 | 6.5 | 1 | 12 | 24 | 0.92
BRUME220 T 3 220/ 70 TFO ¦ | BRUME | BRUME | 220 / T 3 | 225 | 76 |  | 90 |  |  | 15.2 |  |  | 1 | 10 | 17 | -1.37
BRUME380 T 1 380/220/36 TFO ¦ | BRUME | BRUME | 380 / T 1 | 400 | 245 | 36 | 300 | 300 | 15 | 15.4 | 5.5 | 6.9 | 1 | 11 | 24 | 0.87
BRUME380 T 4 380/ 70/36 TFO ¦ | BRUME | BRUME | 380 / T 4 | 400 | 76 | 36 | 110 | 110 | 2 | 20.8 | 1.6 | 2 | 1 | 17 | 33 | -0.94
CHAMP380 T11 380/ 70/36 TFO ¦ | CHAMP | CHAMPION (NAMUR) | 380 / T11 | 400 | 76 | 36 | 220 | 220 | 50 | 20.9 | 6.9 | 12.1 | 1 | 18 | 35 | -0.88
CHAMP380 T12 380/ 70/36 TFO ¦ | CHAMP | CHAMPION (NAMUR) | 380 / T12 | 400 | 76 | 36 | 220 | 220 | 2 | 22.5 | 0.3 | 0.5 | 1 | 17 | 33 | -0.94
DOEL 380 T 5 380/150/36 TFO ¦ | DOEL | DOEL | 380 / T 5 | 400 | 165 | 34 | 150 | 150 | 5 | 15.3 | 1.7 | 0.9 | 1 | 12 | 24 | 1
DROGE380 T 4 380/150/36 TFO ¦ | DROGE | DROGENBOS | 380 / T 4 | 400 | 165 | 34 | 500 | 500 | 15 | 19.8 | 1.2 | 2.1 | 1 | 12 | 24 | -1.01
EEKLN380 T 1 380/150/36 TFO ¦ | EEKLN | EEKLO NOORD | 380 / T 1 | 400 | 165 | 34 | 450 | 450 | 15 | 17.7 | 1.3 | 2.2 | 1 | 12 | 24 | 1.01
GOUY 380 T 3 380/150/36 TFO ¦ | GOUY | GOUY | 380 / T 3 | 400 | 165 | 34 | 450 | 450 | 15 | 18.1 | 1.2 | 2.2 | 1 | 12 | 24 | 1.01
GOUY 380 T 4 380/150/36 TFO ¦ | GOUY | GOUY | 380 / T 4 | 400 | 165 | 34 | 450 | 450 | 15 | 18 | 1.2 | 2.1 | 1 | 12 | 24 | 1.01
GRAMM380 T 1 380/150/36 TFO ¦ | GRAMM | GRAMME | 380 / T 1 | 400 | 158 | 35 | 450 | 450 | 150 | 18.3 | 12.8 | 22.7 | 1 | 12 | 24 | 1.09
HEINS220 T11 220/ 70/15 TFO ¦ | HEINS | HEINSCH | 220 / T11 | 225 | 72 | 16 | 90 | 90 | 30 | 11.5 | 7.7 | 12.2 | 1 | 7 | 19 | -1.67
HOUFF220 T11 220/ 70/15 TFO ¦ | HOUFF | HOUFFALIZE | 220 / T11 | 225 | 74 | 16 | 60 | 60 | 20 | 11.4 | 23.5 | 12.2 | 1 | 7 | 19 | -1.67
IZGEM380 T 1 380/150/36 TFO ¦ | IZGEM | IZEGEM | 380 / T 1 | 400 | 165 | 34 | 500 | 500 | 15 | 19.7 | 1.2 | 2.1 | 1 | 12 | 24 | 1.01
IZGEM380 T 2 380/150/36 TFO ¦ | IZGEM | IZEGEM | 380 / T 2 | 400 | 165 | 34 | 450 | 450 | 15 | 17.6 | 1.3 | 2.2 | 1 | 12 | 24 | 1.01
JUPIL220 T 1 220/150/15 TFO ¦ | JUPIL | JUPILLE | 220 / T 1 | 236 | 165 | 16 | 300 | 300 | 50 | 13.3 | 0.7 | 1 | 1 | 11 | 21 | 2
JUPIL220 T 5 220/ 70/70 TFO ¦ | JUPIL | JUPILLE | 220 / T 5 | 225 | 72 | 72 | 160 | 80 | 80 | 13.9 | 29.1 | 14 | 1 | 13 | 19 | 1.25
JUPIL220 T 7 220/150/15 TFO ¦ | JUPIL | JUPILLE | 220 / T 7 | 236 | 156 | 16 | 300 | 300 | 50 | 12 | 15.4 | 18.5 | 1 | 7 | 13 | 2
LINT 380 T 1 380/150/36 TFO ¦ | LINT | LINT | 380 / T 1 | 400 | 165 | 34 | 450 | 450 | 15 | 18 | 1.2 | 2.1 | 1 | 12 | 24 | 1.01
LINT 380 T 2 380/150/36 TFO ¦ | LINT | LINT | 380 / T 2 | 400 | 165 | 34 | 450 | 450 | 15 | 17.6 | 1.3 | 2.2 | 1 | 12 | 24 | 1.01
LIXHE220 T 7 220/150/15 TFO ¦ | LIXHE | LIXHE | 220 / T 7 | 236 | 156 | 16 | 300 | 300 | 50 | 12 | 16.3 | 19.2 | 1 | 7 | 13 | 2
LIXHE380 T 6 380/220/36 TFO ¦ | LIXHE | LIXHE | 380 / T 6 | 400 | 246 | 36 | 300 | 300 | 15 | 14.6 | 3.9 | 4.9 | 1 | 11 | 24 | 0.99
LIXHE380 T11 380/220/36 TFO ¦ | LIXHE | LIXHE | 380 / T11 | 400 | 246 | 36 | 300 | 300 | 15 | 14.6 | 3.9 | 5 | 1 | 11 | 24 | 0.99
MARCO220 T11 220/ 70/15 TFO ¦ | MARCO | MARCOURT | 220 / T11 | 220 | 73 | 17 | 85 | 85 | 20 | 11.3 | 7.7 | 8.9 | 1 | 12 | 26 | -1.05
MASSE380 T 1 380/150/36 TFO ¦ | MASSE | MASSENHOVEN | 380 / T 1 | 400 | 165 | 34 | 450 | 450 | 15 | 18.1 | 1.2 | 2.1 | 1 | 12 | 24 | 1.01
MEERH380 T 1 380/150/36 TFO ¦ | MEERH | MEERHOUT | 380 / T 1 | 400 | 159 | 35 | 465 | 465 | 158 | 18.6 | 13.2 | 23.1 | 1 | 12 | 24 | 1.09
MEERH380 T 2 380/150/36 TFO ¦ | MEERH | MEERHOUT | 380 / T 2 | 400 | 165 | 34 | 500 | 500 | 15 | 19.8 | 1.2 | 2.1 | 1 | 12 | 24 | 1.01
MERCA380 T 1 380/150/36 TFO ¦ | MERCA | MERCATOR | 380 / T 1 | 400 | 158 | 35 | 450 | 450 | 150 | 18.2 | 12.6 | 22 | 1 | 12 | 24 | 1.09
MERCA380 T 2 380/150/36 TFO ¦ | MERCA | MERCATOR | 380 / T 2 | 400 | 165 | 34 | 555 | 555 | 15 | 22.9 | 1.3 | 2.1 | 1 | 12 | 24 | 1
MONCE220 T12 220/150/ 6 TFO ¦ | MONCE | MONCEAU | 220 / T12 | 225 | 155 | 6 | 290 | 290 | 20 | 10.4 | 22.1 | 24.5 | 1 | 10 | 19 | 1.33
RIMIE220 T 3 220/ 70/70 TFO ¦ | RIMIE | RIMIERE | 220 / T 3 | 225 | 72 | 72 | 160 | 80 | 80 | 12.7 | 20.7 | 12.6 | 1 | 11 | 21 | 1.7
RIMIE380 T 8 380/220/36 TFO ¦ | RIMIE | RIMIERE | 380 / T 8 | 400 | 245 | 36 | 300 | 300 | 50 | 14.6 | 11 | 15.7 | 1 | 11 | 24 | 0.86
RIMIE380 T 9 380/220/36 TFO ¦ | RIMIE | RIMIERE | 380 / T 9 | 400 | 245 | 35 | 300 | 300 | 15 | 14.6 | 3 | 3 | 1 | 11 | 24 | 0.99
RIMIE380 T 9 380/220/36 TFO ¦ | RIMIE | RIMIERE | 380 / T 9 | 400 | 245 | 35 | 300 | 300 | 15 | 14.6 | 3 | 3 | 1 | 11 | 24 | 0.99
RODEN380 T 1 380/150/36 TFO ¦ | RODEN | RODENHUIZE | 380 / T 1 | 400 | 165 | 34 | 450 | 450 | 15 | 18 | 1.2 | 2.2 | 1 | 12 | 24 | 1.01
ROMSE220 T 8 220/ 70/15 TFO ¦ | ROMSE | ROMSEE | 220 / T 8 | 225 | 72 | 16 | 90 | 90 | 30 | 11.4 | 7.8 | 11.4 | 1 | 7 | 19 | -1.67
SERAI220 T 1 220/ 70/70 TFO ¦ | SERAI | SERAING (ARCELORMITTAL) | 220 / T 1 | 225 | 72 | 72 | 160 | 80 | 80 | 12.5 | 20.8 | 12.5 | 1 | 11 | 21 | 1.7
SERAI220 T 2 220/ 70/ 6 TFO ¦ | SERAI | SERAING (ARCELORMITTAL) | 220 / T 2 | 208 | 70 | 6 | 90 | 90 | 30 | 15.2 | 36.2 | 36.2 | 1 | 7 | 19 | 1.37
STEVN380 T 1 380/150/36 TFO ¦ | STEVN | STEVIN | 380 / T 1 | 400 | 165 | 36 | 555 | 555 | 75 | 21.5 | 1.2 | 2 | 1 | 12 | 24 | 0.92
STEVN380 T 2 380/150/36 TFO ¦ | STEVN | STEVIN | 380 / T 2 | 400 | 165 | 36 | 555 | 555 | 75 | 21.6 | 1.2 | 2 | 1 | 12 | 24 | 0.92
STEVN380 T 3 380/220/36 TFO ¦ | STEVN | STEVIN | 380 / T 3 | 400 | 225 | 36 | 600 | 600 | 15 | 14.9 | 3.4 | 3.8 | 1 | 6 | 21 | 0.92
STEVN380 T 4 380/220/36 TFO ¦ | STEVN | STEVIN | 380 / T 4 | 400 | 225 | 36 | 600 | 600 | 15 | 14.9 | 3.4 | 3.8 | 1 | 6 | 21 | 0.92
STEVN380 T 5 380/220/36 TFO ¦ | STEVN | STEVIN | 380 / T 5 | 400 | 225 | 36 | 600 | 600 | 15 | 14.9 | 3.4 | 3.8 | 1 | 6 | 21 | 0.92
STEVN380 T 6 380/220/36 TFO ¦ | STEVN | STEVIN | 380 / T 6 | 400 | 225 | 36 | 600 | 600 | 15 | 14.9 | 3.4 | 3.8 | 1 | 6 | 21 | 0.92
TERGN380 T11 380/150/36 TFO ¦ | TERGN | TERGNEE | 380 / T11 | 400 | 165 | 34 | 450 | 450 | 15 | 17.8 | 1.3 | 2.2 | 1 | 12 | 24 | 1.01
TERGN380 T12 380/150 TFO ¦ | TERGN | TERGNEE | 380 / T12 | 400 | 156 |  | 180 |  |  | 6.2 |  |  | 1 | 3 | 5 | 2.5
TIBIS380 T 1 380/150/36 TFO ¦ | TIBIS | TIHANGE BIS | 380 / T 1 | 400 | 165 | 34 | 555 | 555 | 15 | 23 | 1.3 | 2.1 | 1 | 12 | 24 | 1
VANYK380 D 1 380/380 TFO ¦ | VANYK | VAN EYCK | 380 / D 1 | 400 | 400 |  | 1420 |  |  | 9.3 |  |  | 1 | 18 | 35 | 0
VANYK380 D 2 380/380 TFO ¦ | VANYK | VAN EYCK | 380 / D 2 | 400 | 400 |  | 1420 |  |  | 9.3 |  |  | 1 | 18 | 35 | 0
VERBR380 T 1 380/150/36 TFO ¦ | VERBR | VERBRANDE BRUG | 380 / T 1 | 400 | 165 | 34 | 450 | 450 | 15 | 18.1 | 1.2 | 2.1 | 1 | 12 | 24 | 1.01
VERBR380 T 2 380/150/36 TFO ¦ | VERBR | VERBRANDE BRUG | 380 / T 2 | 400 | 165 | 34 | 555 | 555 | 15 | 23 | 1.3 | 2.1 | 1 | 12 | 24 | 1
VILLE220 T 1 220/ 70/15 TFO ¦ | VILLE | VILLEROUX | 220 / T 1 | 220 | 74 | 16 | 85 | 85 | 20 | 11.8 | 6.8 | 10.1 | 1 | 12 | 25 | -1.05
VILLE220 T 4 220/ 70/15 TFO ¦ | VILLE | VILLEROUX | 220 / T 4 | 220 | 70 | 16 | 90 | 90 | 5 | 11.3 | 5 | 4.1 | 1 | 11 | 21 | -1.5
ZANDV380 D 1 380/380 TFO ¦ | ZANDV | ZANDVLIET | 380 / D 1 | 400 | 400 |  | 1400 |  |  | 9.3 |  |  | 1 | 18 | 35 | 0
ZANDV380 D 2 380/380 TFO ¦ | ZANDV | ZANDVLIET | 380 / D 2 | 400 | 400 |  | 1400 |  |  | 9.3 |  |  | 1 | 18 | 35 | 0
ZANDV380 T 1 380/150/36 TFO ¦ | ZANDV | ZANDVLIET | 380 / T 1 | 400 | 165 | 34 | 500 | 500 | 15 | 19.9 | 1.2 | 2.2 | 1 | 12 | 24 | 1.01
ZANDV380 T 2 380/150/36 TFO ¦ | ZANDV | ZANDVLIET | 380 / T 2 | 400 | 165 | 34 | 555 | 555 | 15 | 22.3 | 1.1 | 2 | 1 | 12 | 24 | 1.09