## Contents
Adequacy and Flexibility study 2024-2034 - CENTRAL scenario and data
This data is provided in the framework of the Adequacy and Flexibility study covering the years from 2024 to 2034. This study has been published on 29 of June 2023.
The assumptions were subject to a public consultation in November 2022 (see BOX 1-2 of the study report)
This Excel file contains the data related to the scenario framework of the study including economic and flexibility aspects. For further details on the data and assumptions, please refer to the study report.
Online published study report:
Adequacy studies (elia.be)
Input data for market and flexibility simulations
1. Generation
1.1. Invidividually modelled thermal generation
1.2. Renewable energy sources and decentralised thermal production
2. Demand
2.1. Total electricity demand
3. Flexibility
3.1. Storage
3.2. DSR industry
3.3. DSR end-user
3.4. Electrolysers
4. Economic and technical variables
4.1. Fuel and CO2 prices
4.2. Investment costs
4.3. Outages
4.4. Short-term flexibility characteristics
5. Flow-based domains
5.1. Main assumptions for flow-based domains
6. Other countries
6.1. Data for other countries

## 1.1. Indiv. mod. thermal gen.
1.1. Individually modelled thermal generation
This section concerns large thermal production units that are all individually modelled in the simulations.
This information is based on official information known in February 2023. | [7 empty] | Color Legend
Note that exact expected commissioning and decommissioning dates are taken into account. | [7 empty] | Units that were not part of the EVA as they were not indicated by market parties to be at risk or that the support mechanism was to be stopped in the future
Units that are not available for the market or closed
Units that were part of the Economic Viability Assessment (EVA)
Available units and no EVA were performed (nuclear)
Available units and no EVA were performed (new CCGT)
Situation at end of the given year - considered as available for the EVA/market
Owner | Production unit name | Type | CHP | Fuel type | Net generation capacity [MW] | Efficiency [%] | VOM [€/MWh] | Considered in the Economic Viability Assessment (EVA) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Comments
Engie - Electrabel | AALTER TJ | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AMERCOEUR 1 GT | CCGT-GT |  | Gas | 289 | 58% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AMERCOEUR 1 ST | CCGT-ST |  | Gas | 162 | 58% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AWIRS 4 | CL |  | Biomass | 75 | 38% | 3.6 | - | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/09/2020 - https://economie.fgov.be/sites/default/files/Files/Energy/Mise-arret-definitive-unite-Awirs-4.pdf
Engie - Electrabel | Flémalle NEW | CCGT |  | Gas | 890 | 61% | 2.4 | No | no | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results
Engie - Electrabel | BEERSE TJ | TJ |  | Oil | 32 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | Beveren 2 Indaver | IS |  | Waste | 21 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | Beveren 3 Indaver | IS |  | Waste | 24 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | Beveren Ineos Phenol Chem | OCGT | x | Gas | 25.1 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | Beveren Sleco | IS |  | Waste | 41 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biopower | BIOMASSA OOSTENDE | IS |  | Biomass | 18 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biostoom | BIOSTOOM OOSTENDE | IS |  | Waste | 19.4 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Borealis | Borealis Kallo Cogen GT_ST | CCGT | x | Gas | 32 | 45% | 2.4 | No | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Commissioning date expected - mid-2024 (01/07/2024 considered) https://www.spglobal.com/commodityinsights/en/market-insights/latest-news/petrochemicals/090122-pdh-project-in-belgium-delayed-to-mid-2024-as-borealis-retenders-construction-contracts
Engie - Electrabel | CIERREUX TJ | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | DOEL 1 | NU |  | Nuclear | 445 | 33% | 10.8 | No | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 15/02/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | DOEL 2 | NU |  | Nuclear | 445 | 33% | 10.8 | No | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/12/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | DOEL 3 | NU |  | Nuclear | 1006 | 33% | 10.8 | No | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2022 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | DOEL 4 | NU |  | Nuclear | 1039 | 33% | 10.8 | No | yes | yes | yes | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | Lifetime extension - Considered operational for winter 2026-27
Engie - Electrabel | DROGENBOS GT1 | CCGT-GT |  | Gas | 150 | 52% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | DROGENBOS GT2 | CCGT-GT |  | Gas | 150 | 52% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | DROGENBOS ST | CCGT-ST |  | Gas | 160 | 52% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 31 | OCGT |  | Gas | 25 | 30% | 13.2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 32 | OCGT |  | Gas | 25 | 30% | 13.2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 41 | OCGT |  | Gas | 64 | 42% | 13.2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | ANGLEUR TG 42 | OCGT |  | Gas | 64 | 42% | 13.2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | HAM 31 | OCGT |  | Gas | 58 | 42% | 13.2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | HAM 32 | OCGT |  | Gas | 58 | 42% | 13.2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | HAM Gent-GT | CCGT | x | Gas | 39 | 45% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | RINGVAART STEG | CCGT |  | Gas | 385 | 55% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | SERAING TG1 | CCGT-GT |  | Gas | 150 | 52%* | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Efficiency of 34,4 % considered as of 18/04/2024 when TGV closes
Luminus | SERAING TG2 | CCGT-GT |  | Gas | 150 | 52%* | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Efficiency of 34,4 % considered as of 18/04/2024 when TGV closes
Luminus | EDF Luminus Seraing ST | CCGT-ST |  | Gas | 170 | 52% | 2.4 | Yes | yes | yes | no | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 18/04/2024 - https://economie.fgov.be/sites/default/files/Files/Energy/tijdelijke-buitenwerkingstelling-stoomturbinesteg-centrale-seraing.pdf
Luminus | EDF Luminus Seraing NEW | CCGT |  | Gas | 885 | 61% | 2.4 | No | no | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results
Euro-silo | Euro-Silo | CCGT | x | Gas | 12.9 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Indaver | E-wood | IS |  | Waste | 22 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | E-wood production unit came in operation in December 2022.
Engie - Electrabel | Fluxys Zeebrugge | OCGT | x | Gas | 40 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Green Power | Greenpower Oostende | IS | x | Waste | 20 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | HERDERSBRUG GT1 | CCGT-GT |  | Gas | 157 | 51% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | HERDERSBRUG GT2 | CCGT-GT |  | Gas | 156.3 | 51% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | HERDERSBRUG ST | CCGT-ST |  | Gas | 167 | 51% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO GT1 | CCGT-GT | x | Gas | 44.8 | 58% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO GT2 | CCGT-GT | x | Gas | 44.8 | 58% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INEOS | INESCO ST | CCGT-ST | x | Gas | 48.5 | 58% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INTRADEL | INTRADEL | IS |  | Waste | 32 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IPALLE | Ipalle THUMAIDE | IS |  | Waste | 34 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ISVAG | IS |  | Waste | 12 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lampiris | IVBO | IS |  | Waste | 16 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Luminus | IZEGEM | CCGT | x | Gas | 20 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE GT1 | CCGT-GT | x | Gas | 48 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE GT2 | CCGT-GT | x | Gas | 48 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Inovyn | JEMEPPE-SUR-SAMBRE ST | CCGT-ST | x | Gas | 10 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa GT1 | CCGT-GT | x | Gas | 43 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa GT2 | CCGT-GT | x | Gas | 32 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Energy | Lillo Degussa ST | CCGT-ST | x | Gas | 10 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Direct Energie | MARCINELLE ENERGIE TGV | CCGT |  | Gas | 413 | 52% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | MONSANTO LILLO WKK EBL | OCGT | x | Gas | 43 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | NOORDSCHOTE TJ | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | Oorderen Bayer | OCGT | x | Gas | 43 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | RODENHUIZE 4 | CL |  | Biomass | 205 | 38% | 3.6 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | As of 24.02.23 Rodenhuize 4 will be used as a backup unit to Zelzate Knippegroen for burning steel gas when Zelzate is unavailable - https://umm.nordpoolgroup.com/#/messages/73aa666e-c3ff-4224-a1e5-6ad751abf122/1
Engie - Electrabel | SAINT-GHISLAIN STEG | CCGT |  | Gas | 378 | 51% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Capacity updated from 350 to 378 MW - https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2022/20220620_engie---non-confidential-parts.pdf
Engie - Electrabel | SAPPI LANAKEN GT | OCGT | x | Gas | 43 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Centre de Tri | Schaerbeek SIOMAB 1 | IS |  | Waste | 15 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Centre de Tri | Schaerbeek SIOMAB 2 | IS |  | Waste | 15 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Centre de Tri | Schaerbeek SIOMAB 3 | IS |  | Waste | 15 | 36% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EXXONMOBIL | SCHELDELAAN EXXONMOBIL | CCGT | x | Gas | 140 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE CHP 1 | CL | x | Biomass | 10 | 38% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA | STORA LANGERBRUGGE CHP 2 | CL | x | Biomass | 40 | 38% | 3.6 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AALST SYRAL GT | CCGT-GT | x | Gas | 43 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | AALST SYRAL ST | CCGT-ST | x | Gas | 5 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TAMINCO | TAMINCO GENT CHP | OCGT | x | Gas | 6.3 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | TIHANGE 1N | NU |  | Nuclear | 481 | 33% | 10.8 | No | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | TIHANGE 1S | NU |  | Nuclear | 481 | 33% | 10.8 | No | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | TIHANGE 2 | NU |  | Nuclear | 1008 | 33% | 10.8 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/02/2023 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
Engie - Electrabel | Tihange 3 | NU |  | Nuclear | 1038 | 33% | 10.8 | No | yes | yes | yes | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | Lifetime extension - Considered operational for winter 26-27
T-Power | T-POWER | CCGT |  | Gas | 425 | 58% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | TURBOJET VOLTA | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | no | no | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 26/08/2023 - https://economie.fgov.be/sites/default/files/Files/Energy/22-54-EBL-FOD-N-Mahieu-fermeture-TJ-VOLTA-Art4-%20GHS-signed.pdf
Engie - Electrabel | VILVOORDE GT | CCGT-GT |  | Gas | 255 | 37%* | 2.4 | No | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 31/10/2025 - https://economie.fgov.be/sites/default/files/Files/Energy/21-34-EBL-SPF-mise-a-l-arret-definitive-central-de-Vilvoorde.pdf. Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
Engie - Electrabel | VILVOORDE ST | CCGT-ST |  | Gas | 105 | 37%* | 2.4 | No | yes | no | no | no | no | no | no | no | no | no | no | no | no | Based on REMIT information, decommissioning 01/04/2023. Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
TOTAL | WILMARSDONK TOTAL GT1 | OCGT | x | Gas | 43 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TOTAL | WILMARSDONK TOTAL GT2 | OCGT | x | Gas | 43 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TOTAL | WILMARSDONK TOTAL GT3 | OCGT | x | Gas | 43 | 41% | 13.2 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zandvliet Power NV | ZANDVLIET POWER | CCGT | x | Gas | 419 | 57% | 2.4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | A repowering to 419 MW as of November 2024 is announced on REMIT (386 MW is considered for winter 2023-2024)
Engie - Electrabel | ZEDELGEM TJ | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ZEEBRUGGE TJ | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | KNIPPEGROEN STEG | CL |  | Gas | 305 | 42% | 3.6 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | ZELZATE TJ | TJ |  | Oil | 18 | 26% | 4 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | Zwijndrecht Lanxess GT | CCGT-GT | x | Gas | 43 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Engie - Electrabel | Zwijndrecht Lanxess ST | CCGT-ST | x | Gas | 15 | 45% | 2.4 | No | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Legend Unit-Type
CCGT | Combined Cycle
CCGT-GT | Combined Cycle - Gas Turbine
CCGT-ST | Combined Cycle - Steam Turbine
OCGT | Open Cycle Gas Turbine
CL | Classic
GT | Gas Turbine
ST | Steam Turbine
IS | Incineration Station
NU | Nuclear
TJ | TurboJet
CHP | Cogeneration Unit

## 1.1. Ind. mod. thermal prod OLD (hidden)
1.1. Individually modelled thermal generation
Yellow cells are indicating changes compared to Excel file submitted to public consultation in October 2022.
| Sources | [7 empty] | Color Legend
| - This information is based on official information known. | [7 empty] | Units that will not be part of the EVA unless are indicated by market parties to be at risk or that the support mechanism is to be stopped in the future
| - Please inform us if any unit(s) are to be considered as not available for future time horizons or if any of those units are at risk of not being available and for which reasons. | [7 empty] | Units that are not available for the market or closed
Units will be part of the Economic Viability Assessment (EVA)
| Note that exact expected commissioning and decommissioning date are taken into account. | [7 empty] | Available units and no EVA will be performed (nuclear)
Available units and no EVA will be performed (new CCGT)
Situation at end of the given year - considered as available for the EVA/market
AF23 PC name | Owner | Production unit name | Type | CHP | Fuel type | Net generation capacity [MW] | Efficiency [%] | VOM [€/MWh] | Proposal to be considered in the Economic Viability Assessment (EVA) | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Comments
AALTER TJ | Engie electrabel | AALTER TJ | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
AMERCOEUR 1R GT | Engie electrabel | AMERCOEUR 1R GT | CCGT-GT |  | Gas | 289 | 58% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
AMERCOEUR 1R ST_cur | Engie electrabel | AMERCOEUR 1R ST_cur | CCGT-ST |  | Gas | 162 | 58% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
AWIRS 4 | Engie electrabel | AWIRS 4 | CL |  | Biomass | 75 | 38% | 3 | - | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/09/2020 - https://economie.fgov.be/sites/default/files/Files/Energy/Mise-arret-definitive-unite-Awirs-4.pdf
Flémalle NEW | Engie electrabel | Flémalle NEW | CCGT |  | Gas | 890 | 61% | 2 | No | no | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results
BEERSE TJ | Engie electrabel | BEERSE TJ | TJ |  | Oil | 32 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Beveren 2 Indaver | Indaver | Beveren 2 Indaver | IS |  | Waste | 21 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Beveren 3 Indaver | Indaver | Beveren 3 Indaver | IS |  | Waste | 24 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Beveren Ineos Phenol Chem | Engie electrabel | Beveren Ineos Phenol Chem | GT | x | Gas | 25.1 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Beveren Sleco | Indaver | Beveren Sleco | IS |  | Waste | 41 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biomassa Oostende | Biopower | Biomassa Oostende | IS |  | Biomass | 18 | 42% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Biostoom Oostende | Biostoom | Biostoom Oostende | IS |  | Waste | 19.4 | 42% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Borealis Kallo Cogen GT_ST | Borealis | Borealis Kallo Cogen GT_ST | CCGT | x | Gas | 32 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Commissioning date expected - mid-2024 (01/07/2024 considered) https://www.spglobal.com/commodityinsights/en/market-insights/latest-news/petrochemicals/090122-pdh-project-in-belgium-delayed-to-mid-2024-as-borealis-retenders-construction-contracts
CIERREUX TJ | Engie electrabel | CIERREUX TJ | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
DOEL 1 | Engie electrabel | DOEL 1 | NU |  | Nuclear | 445 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 15/02/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
DOEL 2 | Engie electrabel | DOEL 2 | NU |  | Nuclear | 445 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/12/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
DOEL 3 | Engie electrabel | DOEL 3 | NU |  | Nuclear | 1006 | 33% | 9 | No - based on the law (official closure dates taken into account) | no | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2022 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
DOEL 4 | Engie electrabel | DOEL 4 | NU |  | Nuclear | 1039 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | yes | yes | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | Lifetime extension - Considered operational for winter 26-27
DROGENBOS GT1 | Engie electrabel | DROGENBOS GT1 | CCGT-GT |  | Gas | 150 | 52% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
DROGENBOS GT2 | Engie electrabel | DROGENBOS GT2 | CCGT-GT |  | Gas | 150 | 52% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
DROGENBOS ST | Engie electrabel | DROGENBOS ST | CCGT-ST |  | Gas | 160 | 52% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Angleur GT31 | Luminus | EDF Luminus Angleur GT31 | GT |  | Gas | 25 | 30% | 11 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Angleur GT32 | Luminus | EDF Luminus Angleur GT32 | GT |  | Gas | 25 | 30% | 11 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Angleur GT41 | Luminus | EDF Luminus Angleur GT41 | GT |  | Gas | 64 | 42% | 11 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Angleur GT42 | Luminus | EDF Luminus Angleur GT42 | GT |  | Gas | 64 | 42% | 11 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Ham GT31 | Luminus | EDF Luminus Ham GT31 | GT |  | Gas | 58 | 42% | 11 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Ham GT32 | Luminus | EDF Luminus Ham GT32 | GT |  | Gas | 58 | 42% | 11 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Ham STEG | Luminus | EDF Luminus Ham STEG | CCGT | x | Gas | 39 | 41% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Ringvaart STEG | Luminus | EDF Luminus Ringvaart STEG | CCGT |  | Gas | 385 | 55% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
EDF Luminus Seraing GT1 | Luminus | EDF Luminus Seraing GT1 | CCGT-GT |  | Gas | 150 | 52%* | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Efficiency of 37% as of 18/04/2024 when TGV closes (based on Vilvoorde efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
EDF Luminus Seraing GT2 | Luminus | EDF Luminus Seraing GT2 | CCGT-GT |  | Gas | 150 | 52%* | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Efficiency of 37% as of 18/04/2024 when TGV closes (based on Vilvoorde efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
EDF Luminus Seraing ST | Luminus | EDF Luminus Seraing ST | CCGT-ST |  | Gas | 170 | 52% | 2 | Yes | yes | yes | no | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 18/04/2024 - https://economie.fgov.be/sites/default/files/Files/Energy/tijdelijke-buitenwerkingstelling-stoomturbinesteg-centrale-seraing.pdf
EDF Luminus Seraing NEW | Luminus | EDF Luminus Seraing NEW | CCGT |  | Gas | 885 | 61% | 2 | No | no | no | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Contracted in the CRM Y-4 auction for Delivery Period 2025-26 for a duration of 15 years - https://www.elia.be/en/grid-data/adequacy/crm-auction-results
Euro-Silo | Euro-silo | Euro-Silo | CCGT | x | Gas | 12.9 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
E-wood | Indaver | E-wood | IS |  | Waste | 22 | 42% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | E-wood production unit came in operation in December 2022.
Fluxys LNG Zeebrugge WKK | Engie electrabel | Fluxys LNG Zeebrugge WKK | GT | x | Gas | 40 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Greenpower Oostende | Green Power | Greenpower Oostende | IS | x | Waste | 20 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
HERDERSBRUG GT1 | Engie electrabel | HERDERSBRUG GT1 | CCGT-GT |  | Gas | 157 | 51% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
HERDERSBRUG GT2 | Engie electrabel | HERDERSBRUG GT2 | CCGT-GT |  | Gas | 156.3 | 51% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
HERDERSBRUG ST | Engie electrabel | HERDERSBRUG ST | CCGT-ST |  | Gas | 167 | 51% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INESCO GT1 | INEOS | INESCO GT1 | CCGT-GT | x | Gas | 44.8 | 58% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INESCO GT2 | INEOS | INESCO GT2 | CCGT-GT | x | Gas | 44.8 | 58% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
INESCO ST | INEOS | INESCO ST | CCGT-ST | x | Gas | 48.5 | 58% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Intradel Herstal IS | INTRADEL | Intradel Herstal IS | IS |  | Waste | 32 | 23% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Ipalle Thumaide | IPALLE | Ipalle Thumaide | IS |  | Waste | 34 | 23% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
ISVAG | Engie electrabel | ISVAG | IS |  | Waste | 12 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IVBO | IVBO | IVBO | IS |  | Waste | 16 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
IZEGEM | Luminus | IZEGEM | CCGT | x | Gas | 20 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Jemeppe-sur-Sambre GT1 | Inovyn | Jemeppe-sur-Sambre GT1 | CCGT-GT | x | Gas | 48 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Jemeppe-sur-Sambre GT2 | Inovyn | Jemeppe-sur-Sambre GT2 | CCGT-GT | x | Gas | 48 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Jemeppe-sur-Sambre ST | Inovyn | Jemeppe-sur-Sambre ST | CCGT-ST | x | Gas | 10 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Degussa GT1 | Lillo Energy | Lillo Degussa GT1 | CCGT-GT | x | Gas | 43 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Degussa GT2 | Lillo Energy | Lillo Degussa GT2 | CCGT-GT | x | Gas | 32 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Lillo Degussa ST | Lillo Energy | Lillo Degussa ST | CCGT-ST | x | Gas | 10 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Marcinelle Energie TGV | Direct Energie | Marcinelle Energie TGV | CCGT |  | Gas | 413 | 52% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Monsanto Lillo WKK EBL | Engie electrabel | Monsanto Lillo WKK EBL | GT | x | Gas | 43 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
NOORDSCHOTE TJ | Engie electrabel | NOORDSCHOTE TJ | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Oorderen Bayer | Engie electrabel | Oorderen Bayer | GT | x | Gas | 43 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
RODENHUIZE 4 | Engie electrabel | RODENHUIZE 4 | CL |  | Biomass | 205 | 38% | 3 | - | yes | no | no | no | no | no | no | no | no | no | no | no | no | As of 24.02.23 Rodenhuize 4 will be used as a backup unit to Zelzate Knippegroen for burning steel gas when Zelz is unavailable - https://umm.nordpoolgroup.com/#/messages/73aa666e-c3ff-4224-a1e5-6ad751abf122/1
SAINT-GHISLAIN STEG | Engie electrabel | SAINT-GHISLAIN STEG | CCGT |  | Gas | 378 | 51% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | Capacity updated from 350 to 378 MW - https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2022/20220620_engie---non-confidential-parts.pdf
Sappi Lanaken GT | Engie electrabel | Sappi Lanaken GT | GT | x | Gas | 43 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
SCHAERBEEK SIOMAB ST1 | Engie electrabel | SCHAERBEEK SIOMAB ST1 | IS |  | Waste | 15 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
SCHAERBEEK SIOMAB ST2 | Engie electrabel | SCHAERBEEK SIOMAB ST2 | IS |  | Waste | 15 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
SCHAERBEEK SIOMAB ST3 | Engie electrabel | SCHAERBEEK SIOMAB ST3 | IS |  | Waste | 15 | 36% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Scheldelaan Exxonmobil | EXXONMOBIL | Scheldelaan Exxonmobil | GT | x | Gas | 140 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA LANGERBRUGGE WKK1 | STORA | STORA LANGERBRUGGE WKK1 | ST | x | Biomass | 10 | 20% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
STORA LANGERBRUGGE WKK2 | STORA | STORA LANGERBRUGGE WKK2 | ST | x | Biomass | 40 | 20% | 3 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Syral Aalst GT | Engie electrabel | Syral Aalst GT | CCGT-GT | x | Gas | 43 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Syral Aalst ST | Engie electrabel | Syral Aalst ST | CCGT-ST | x | Gas | 5 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TAMINCO Gent WKK | TAMINCO | TAMINCO Gent WKK | GT | x | Gas | 6.3 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TIHANGE 1N | Engie electrabel | TIHANGE 1N | NU |  | Nuclear | 481 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
TIHANGE 1S | Engie electrabel | TIHANGE 1S | NU |  | Nuclear | 481 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/10/2025 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
TIHANGE 2 | Engie electrabel | TIHANGE 2 | NU |  | Nuclear | 1008 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | no | no | no | no | no | no | no | no | no | no | no | no | Decommissioning: 01/02/2023 - https://economie.fgov.be/fr/themes/energie/sources-denergie/nucleaire/base-legale-de-la-sortie-du
TIHANGE 3 | Engie electrabel | TIHANGE 3 | NU |  | Nuclear | 1038 | 33% | 9 | No - based on the law (official closure dates taken into account) | yes | yes | yes | no | yes | yes | yes | yes | yes | yes | yes | yes | yes | Lifetime extension - Considered operational for winter 26-27
T-Power | T-Power | T-Power | CCGT |  | Gas | 425 | 58% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
TURBOJET VOLTA | Engie electrabel | TURBOJET VOLTA | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | no | no | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 26/08/2023 - https://economie.fgov.be/sites/default/files/Files/Energy/22-54-EBL-FOD-N-Mahieu-fermeture-TJ-VOLTA-Art4-%20GHS-signed.pdf
Vilvoorde GT | Engie electrabel | Vilvoorde GT | CCGT-GT |  | Gas | 255 | 37%* | 2 | - | yes | yes | yes | no | no | no | no | no | no | no | no | no | no | Art. 4bis - Decommissioning date: 31/10/2025 - https://economie.fgov.be/sites/default/files/Files/Energy/21-34-EBL-SPF-mise-a-l-arret-definitive-central-de-Vilvoorde.pdf. Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
Vilvoorde ST | Engie electrabel | Vilvoorde ST | CCGT-ST |  | Gas | 105 | 37%* | 2 | - | yes | no | no | no | no | no | no | no | no | no | no | no | no | Based on REMIT information, decommissioning 01/04/2023. Efficiency as OCGT https://flux50.com/media/2962/Rudi%20Hermans%2020190117.pdf
Wilmarsdonk Total GT1 | TOTAL | Wilmarsdonk Total GT1 | GT | x | Gas | 43 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Wilmarsdonk Total GT2 | TOTAL | Wilmarsdonk Total GT2 | GT | x | Gas | 43 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Wilmarsdonk Total GT3 | TOTAL | Wilmarsdonk Total GT3 | GT | x | Gas | 43 | 41% | 11 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zandvliet Power | Zandvliet Power NV | Zandvliet Power | CCGT | x | Gas | 386.2 | 57% | 2 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zedelgem TJ | Engie electrabel | Zedelgem TJ | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zeebrugge TJ | Engie electrabel | Zeebrugge TJ | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zelzate 2 Knippegroen | Engie electrabel | Zelzate 2 Knippegroen | CL |  | Gas | 305 | 42% | 3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zelzate TJ | Engie electrabel | Zelzate TJ | TJ |  | Oil | 18 | 26% | 3.3 | Yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zwijndrecht Lanxess GT | Engie electrabel | Zwijndrecht Lanxess GT | CCGT-GT | x | Gas | 43 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
Zwijndrecht Lanxess ST | Engie electrabel | Zwijndrecht Lanxess ST | CCGT-ST | x | Gas | 15 | 45% | 2 | No, unless elements that the unit is at risk or support mechanism to be ended | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes | yes
0.4
| Legend Unit-Type | [5 empty] | 1.25
| CCGT | Combined Cycle |  |  |  |  | 0.9
| CCGT-GT | Combined Cycle - Gas Turbine
| CCGT-ST | Combined Cycle - Steam Turbine
| CL | Classic
| GT | Gas Turbine
| ST | Steam Turbine
| IS | Incineration Station
| NU | Nuclear
| TJ | TurboJet
| CHP | Cogeneration Unit
| CCGT-CHP | Combined Cycle that can also operate in CHP mode
Change DCO 16/02: - Add CHP column - change CHP type as CCGT / CCGT-GT, CCGT-ST based on the name of the unit - Change GT names to OCGT - Change VOM based on the type of the unit (eg: GT = 11, IS = CL = 3, TJ = 3.3, NU = 9) - Align efficiency of OCGT to MAX 41%
Note on H21: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H25: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H40: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H48: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H68: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H73: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H78: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H79: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf
Note on H82: Author: Unknown efficiency set as 41% (efficiency for GT) as discussed with Raf

## overview thermal (hidden)
| 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Nuclear | 3929 | 3929 | 0 | 2077 | 2077 | 2077 | 2077 | 2077 | 2077 | 2077 | 2077 | 2077
Gas | 5711.7 | 5573.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7 | 7093.7
Biomass | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68
Waste | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4 | 286.4
Oil | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140
| 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Nuclear | 3.929 | 3.929 | 0 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077 | 2.077
Gas | 5.7117 | 5.5737 | 7.0937 | 7.0937 | 7.0937 | 7.0937 | 7.0937 | 7.0937 | 7.0937 | 7.0937 | 7.0937 | 7.0937
Biomass | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068
Waste | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864 | 0.2864
Oil | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14

## Thermal_mapping (hidden)
[8 empty] | Name LCT | Name CRM
ERAA22 | AF_PreCons | AF_PostCons | ERAA22 | EXCEL AF23_PreConsul | EXCEL AF23_PreConsul | AF_PostCons | AF_PostCons | AALTER TJ | AALTER TJ
AALTER TJ | AALTER TJ | AALTER TJ | AALTER TJ | AALTER TJ | AALTER TJ | AALTER TJ | AALTER TJ | AMERCOEUR 1R GT | AMERCOEUR 1 GT
AMERCOEUR 1R GT+ST | AMERCOEUR 1R GT | AMERCOEUR 1 GT | AMERCOEUR 1R GT+ST | #N/A | AMERCOEUR 1R GT | AMERCOEUR 1 GT | AMERCOEUR 1 GT | AMERCOEUR 1R ST_cur | AMERCOEUR 1 ST
AMERCOEUR 1R GT+ST | AMERCOEUR 1R ST_cur | AMERCOEUR 1 ST | AMERCOEUR 1R GT+ST | #N/A | AMERCOEUR 1R ST_cur | AMERCOEUR 1 ST | AMERCOEUR 1 ST | BEERSE TJ | BEERSE TJ
ArcelorMittal Belgium Gent - EBL - Knippegroen STEG | Zelzate 2 Knippegroen | KNIPPEGROEN STEG | ArcelorMittal Belgium Gent - EBL - Knippegroen STEG | #N/A | Zelzate 2 Knippegroen | KNIPPEGROEN STEG | KNIPPEGROEN STEG | Beveren 2 Indaver | Beveren 2 Indaver
ArcelorMittal Belgium Gent - Zelzate TJ | Zelzate TJ | ZELZATE TJ | ArcelorMittal Belgium Gent - Zelzate TJ | #N/A | Zelzate TJ | ZELZATE TJ | ZELZATE TJ | Beveren 3 Indaver | Beveren 3 Indaver
Arlanxeo Zwijndrecht GT+ST | Zwijndrecht Lanxess GT | Zwijndrecht Lanxess GT | Arlanxeo Zwijndrecht GT+ST | #N/A | Zwijndrecht Lanxess GT | Zwijndrecht Lanxess GT | Zwijndrecht Lanxess GT | Beveren Ineos Phenol Chem | Beveren Ineos Phenol Chem
Arlanxeo Zwijndrecht GT+ST | Zwijndrecht Lanxess ST | Zwijndrecht Lanxess ST | Arlanxeo Zwijndrecht GT+ST |  | Zwijndrecht Lanxess ST | Zwijndrecht Lanxess ST | Zwijndrecht Lanxess ST | Beveren Sleco | Beveren Sleco
AWIRS 4 | AWIRS 4 | AWIRS 4 | AWIRS 4 | AWIRS 4 | AWIRS 4 | #N/A | AWIRS 4 | Biomassa Oostende | BIOMASSA OOSTENDE
AWIRS NEW CCGT | Flémalle NEW | Flémalle NEW | AWIRS NEW CCGT | #N/A | Flémalle NEW | #N/A | Flémalle NEW | Biostoom Oostende | BIOSTOOM OOSTENDE
BEERSE TJ | BEERSE TJ | BEERSE TJ | BEERSE TJ | BEERSE TJ | BEERSE TJ | BEERSE TJ | BEERSE TJ | Borealis Kallo Cogen GT_ST | Borealis Kallo Cogen GT_ST
Biomassa Oostende | Biomassa Oostende | BIOMASSA OOSTENDE | Biomassa Oostende | BIOMASSA OOSTENDE | BIOMASSA OOSTENDE | BIOMASSA OOSTENDE | BIOMASSA OOSTENDE | CIERREUX TJ | CIERREUX TJ
Biostoom Oostende | Biostoom Oostende | BIOSTOOM OOSTENDE | Biostoom Oostende | BIOSTOOM OOSTENDE | BIOSTOOM OOSTENDE | BIOSTOOM OOSTENDE | BIOSTOOM OOSTENDE | DOEL 1 | DOEL 1
CIERREUX TJ | CIERREUX TJ | CIERREUX TJ | CIERREUX TJ | CIERREUX TJ | CIERREUX TJ | CIERREUX TJ | CIERREUX TJ | DOEL 2 | DOEL 2
DEUX-ACREN TJ | - | - | DEUX-ACREN TJ | #N/A | - | #N/A | #N/A | DOEL 4 | DOEL 4
DOEL 1 | DOEL 1 | DOEL 1 | DOEL 1 | DOEL 1 | DOEL 1 | DOEL 1 | DOEL 1 | DROGENBOS GT1 | DROGENBOS GT1
DOEL 2 | DOEL 2 | DOEL 2 | DOEL 2 | DOEL 2 | DOEL 2 | DOEL 2 | DOEL 2 | DROGENBOS GT2 | DROGENBOS GT2
DOEL 3 | DOEL 3 | DOEL 3 | DOEL 3 | DOEL 3 | DOEL 3 | #N/A | DOEL 3 | DROGENBOS ST | DROGENBOS ST
DOEL 4 | DOEL 4 | DOEL 4 | DOEL 4 | DOEL 4 | DOEL 4 | DOEL 4 | DOEL 4 | EDF Luminus Angleur GT31 | ANGLEUR TG 31
DROGENBOS GT1+GT2+ST | DROGENBOS GT1 | DROGENBOS GT1 | DROGENBOS GT1+GT2+ST | #N/A | DROGENBOS GT1 | DROGENBOS GT1 | DROGENBOS GT1 | EDF Luminus Angleur GT32 | ANGLEUR TG 32
DROGENBOS GT1+GT2+ST | DROGENBOS GT2 | DROGENBOS GT2 | DROGENBOS GT1+GT2+ST |  | DROGENBOS GT2 | DROGENBOS GT2 | DROGENBOS GT2 | EDF Luminus Angleur GT41 | ANGLEUR TG 41
DROGENBOS GT1+GT2+ST | DROGENBOS ST | DROGENBOS ST | DROGENBOS GT1+GT2+ST |  | DROGENBOS ST | DROGENBOS ST | DROGENBOS ST | EDF Luminus Angleur GT42 | ANGLEUR TG 42
EDF Luminus Angleur GT31 | EDF Luminus Angleur GT31 | ANGLEUR TG 31 | EDF Luminus Angleur GT31 | #N/A | #N/A | #N/A | #N/A | EDF Luminus Ham GT31 | HAM 31
EDF Luminus Angleur GT32 | EDF Luminus Angleur GT32 | ANGLEUR TG 32 | EDF Luminus Angleur GT32 | #N/A | #N/A | #N/A | #N/A | EDF Luminus Ham GT32 | HAM 32
EDF Luminus Angleur GT41 | EDF Luminus Angleur GT41 | ANGLEUR TG 41 | EDF Luminus Angleur GT41 | #N/A | #N/A | #N/A | #N/A | EDF Luminus Ham STEG | HAM Gent-GT
EDF Luminus Angleur GT42 | EDF Luminus Angleur GT42 | ANGLEUR TG 42 | EDF Luminus Angleur GT42 | #N/A | #N/A | #N/A | #N/A | EDF Luminus Ringvaart STEG | RINGVAART STEG
EDF Luminus Ham GT31 | EDF Luminus Ham GT31 | HAM 31 | EDF Luminus Ham GT31 | #N/A | #N/A | #N/A | #N/A | EDF Luminus Seraing GT1 | SERAING TG1
EDF Luminus Ham GT32 | EDF Luminus Ham GT32 | HAM 32 | EDF Luminus Ham GT32 | #N/A | #N/A | #N/A | #N/A | EDF Luminus Seraing GT2 | SERAING TG2
EDF Luminus Ham STEG | EDF Luminus Ham STEG | HAM Gent-GT | EDF Luminus Ham STEG | #N/A | #N/A | #N/A | #N/A | Euro-Silo | Euro-Silo
EDF Luminus Ringvaart STEG | EDF Luminus Ringvaart STEG | RINGVAART STEG | EDF Luminus Ringvaart STEG | #N/A | #N/A | #N/A | #N/A | E-wood | E-wood
EDF Luminus Seraing GT1+GT2 | EDF Luminus Seraing GT1 | SERAING TG1 | EDF Luminus Seraing GT1+GT2 | #N/A | EDF Luminus Seraing GT1 | SERAING TG1 | SERAING TG1 | Fluxys LNG Zeebrugge WKK | Fluxys Zeebrugge
EDF Luminus Seraing GT1+GT2 | EDF Luminus Seraing GT2 | SERAING TG2 | EDF Luminus Seraing GT1+GT2 |  | EDF Luminus Seraing GT2 | SERAING TG2 | SERAING TG2 | Greenpower Oostende | Greenpower Oostende
Euro-Silo | Euro-Silo | Euro-Silo | Euro-Silo | Euro-Silo | Euro-Silo | Euro-Silo | Euro-Silo | HERDERSBRUG GT1 | HERDERSBRUG GT1
Evonik Degussa GT2+ST | Lillo Degussa ST | Lillo Degussa ST | Evonik Degussa GT2+ST | #N/A | Lillo Degussa ST | Lillo Degussa ST | Lillo Degussa ST | HERDERSBRUG GT2 | HERDERSBRUG GT2
Evonik Degussa GT2+ST | Lillo Degussa GT2 | Lillo Degussa GT2 | Evonik Degussa GT2+ST |  | Lillo Degussa GT2 | Lillo Degussa GT2 | Lillo Degussa GT2 | HERDERSBRUG ST | HERDERSBRUG ST
Lillo Energy Degussa GT1 | Lillo Degussa GT1 | Lillo Degussa GT1 | Lillo Energy Degussa GT1 | #N/A | Lillo Degussa GT1 | Lillo Degussa GT1 | Lillo Degussa GT1 | INESCO GT1 | INESCO GT1
Fluxys LNG Zeebrugge WKK | Fluxys LNG Zeebrugge WKK | Fluxys Zeebrugge | Fluxys LNG Zeebrugge WKK | #N/A | #N/A | #N/A | #N/A | INESCO GT2 | INESCO GT2
Greenpower Oostende | Greenpower Oostende | Greenpower Oostende | Greenpower Oostende | Greenpower Oostende | Greenpower Oostende | Greenpower Oostende | Greenpower Oostende | INESCO ST | INESCO ST
HERDERSBRUG GT1+GT2+ST | HERDERSBRUG GT1 | HERDERSBRUG GT1 | HERDERSBRUG GT1+GT2+ST | #N/A | HERDERSBRUG GT1 | HERDERSBRUG GT1 | HERDERSBRUG GT1 | Intradel Herstal IS | INTRADEL
HERDERSBRUG GT1+GT2+ST | HERDERSBRUG GT2 | HERDERSBRUG GT2 | HERDERSBRUG GT1+GT2+ST |  | HERDERSBRUG GT2 | HERDERSBRUG GT2 | HERDERSBRUG GT2 | Ipalle Thumaide | Ipalle THUMAIDE
HERDERSBRUG GT1+GT2+ST | HERDERSBRUG ST | HERDERSBRUG ST | HERDERSBRUG GT1+GT2+ST |  | HERDERSBRUG ST | HERDERSBRUG ST | HERDERSBRUG ST | ISVAG | ISVAG
Indaver-Sleco Doel GEN1 | Beveren Sleco | Beveren Sleco | Indaver-Sleco Doel GEN1 | #N/A | Beveren Sleco | Beveren Sleco | Beveren Sleco | IVBO | IVBO
Indaver-Sleco Doel GEN2 | Beveren 2 Indaver | Beveren 2 Indaver | Indaver-Sleco Doel GEN2 | #N/A | Beveren 2 Indaver | Beveren 2 Indaver | Beveren 2 Indaver | IZEGEM | IZEGEM
Indaver-Sleco Doel GEN3 | Beveren 3 Indaver | Beveren 3 Indaver | Indaver-Sleco Doel GEN3 | #N/A | Beveren 3 Indaver | Beveren 3 Indaver | Beveren 3 Indaver | Jemeppe-sur-Sambre GT1 | JEMEPPE-SUR-SAMBRE GT1
Ineos Phenol Doel WKK | Beveren Ineos Phenol Chem | Beveren Ineos Phenol Chem | Ineos Phenol Doel WKK | #N/A | Beveren Ineos Phenol Chem | Beveren Ineos Phenol Chem | Beveren Ineos Phenol Chem | Jemeppe-sur-Sambre GT2 | JEMEPPE-SUR-SAMBRE GT2
INESCO GT1+GT2+ST | INESCO GT1 | INESCO GT1 | INESCO GT1+GT2+ST | #N/A | INESCO GT1 | INESCO GT1 | INESCO GT1 | Jemeppe-sur-Sambre ST | JEMEPPE-SUR-SAMBRE ST
INESCO GT1+GT2+ST | INESCO GT2 | INESCO GT2 | INESCO GT1+GT2+ST |  | INESCO GT2 | INESCO GT2 | INESCO GT2 | Lillo Degussa GT1 | Lillo Degussa GT1
INESCO GT1+GT2+ST | INESCO ST | INESCO ST | INESCO GT1+GT2+ST |  | INESCO ST | INESCO ST | INESCO ST | Lillo Degussa GT2 | Lillo Degussa GT2
Intradel Herstal IS | Intradel Herstal IS | INTRADEL | Intradel Herstal IS | #N/A | #N/A | #N/A | #N/A | Lillo Degussa ST | Lillo Degussa ST
Ipalle Thumaide GTA1 | Ipalle Thumaide | Ipalle THUMAIDE | Ipalle Thumaide GTA1 | #N/A | Ipalle Thumaide | Ipalle THUMAIDE | Ipalle THUMAIDE | Marcinelle Energie TGV | MARCINELLE ENERGIE TGV
ISVAG | ISVAG | ISVAG | ISVAG | ISVAG | ISVAG | ISVAG | ISVAG | Monsanto Lillo WKK EBL | MONSANTO LILLO WKK EBL
IVBO | IVBO | IVBO | IVBO | IVBO | IVBO | IVBO | IVBO | NOORDSCHOTE TJ | NOORDSCHOTE TJ
IZEGEM | IZEGEM | IZEGEM | IZEGEM | IZEGEM | IZEGEM | IZEGEM | IZEGEM | Oorderen Bayer | Oorderen Bayer
Jemeppe-sur-Sambre GT1+GT2+ST | Jemeppe-sur-Sambre GT1 | JEMEPPE-SUR-SAMBRE GT1 | Jemeppe-sur-Sambre GT1+GT2+ST | #N/A | Jemeppe-sur-Sambre GT1 | JEMEPPE-SUR-SAMBRE GT1 | JEMEPPE-SUR-SAMBRE GT1 | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG
Jemeppe-sur-Sambre GT1+GT2+ST | Jemeppe-sur-Sambre GT2 | JEMEPPE-SUR-SAMBRE GT2 | Jemeppe-sur-Sambre GT1+GT2+ST |  | Jemeppe-sur-Sambre GT2 | JEMEPPE-SUR-SAMBRE GT2 | JEMEPPE-SUR-SAMBRE GT2 | Sappi Lanaken GT | SAPPI LANAKEN GT
Jemeppe-sur-Sambre GT1+GT2+ST | Jemeppe-sur-Sambre ST | JEMEPPE-SUR-SAMBRE ST | Jemeppe-sur-Sambre GT1+GT2+ST |  | Jemeppe-sur-Sambre ST | JEMEPPE-SUR-SAMBRE ST | JEMEPPE-SUR-SAMBRE ST | SCHAERBEEK SIOMAB ST1 | Schaerbeek SIOMAB 1
Oorderen Bayer | Oorderen Bayer | Oorderen Bayer | Oorderen Bayer | Oorderen Bayer | Oorderen Bayer | Oorderen Bayer | Oorderen Bayer | SCHAERBEEK SIOMAB ST2 | Schaerbeek SIOMAB 2
Marcinelle Energie TGV | Marcinelle Energie TGV | MARCINELLE ENERGIE TGV | Marcinelle Energie TGV | MARCINELLE ENERGIE TGV | MARCINELLE ENERGIE TGV | MARCINELLE ENERGIE TGV | MARCINELLE ENERGIE TGV | SCHAERBEEK SIOMAB ST3 | Schaerbeek SIOMAB 3
Monsanto Lillo WKK EBL | Monsanto Lillo WKK EBL | MONSANTO LILLO WKK EBL | Monsanto Lillo WKK EBL | MONSANTO LILLO WKK EBL | MONSANTO LILLO WKK EBL | MONSANTO LILLO WKK EBL | MONSANTO LILLO WKK EBL | Scheldelaan Exxonmobil | SCHELDELAAN EXXONMOBIL
NOORDSCHOTE TJ | NOORDSCHOTE TJ | NOORDSCHOTE TJ | NOORDSCHOTE TJ | NOORDSCHOTE TJ | NOORDSCHOTE TJ | NOORDSCHOTE TJ | NOORDSCHOTE TJ | STORA LANGERBRUGGE WKK1 | STORA LANGERBRUGGE CHP 1
RODENHUIZE 4 | RODENHUIZE 4 | RODENHUIZE 4 | RODENHUIZE 4 | RODENHUIZE 4 | RODENHUIZE 4 | #N/A | RODENHUIZE 4 | STORA LANGERBRUGGE WKK2 | STORA LANGERBRUGGE CHP 2
SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | SAINT-GHISLAIN STEG | Syral Aalst GT | AALST SYRAL GT
Sappi Lanaken GT | Sappi Lanaken GT | SAPPI LANAKEN GT | Sappi Lanaken GT | SAPPI LANAKEN GT | SAPPI LANAKEN GT | SAPPI LANAKEN GT | SAPPI LANAKEN GT | Syral Aalst ST | AALST SYRAL ST
SCHAERBEEK SIOMAB ST1 | SCHAERBEEK SIOMAB ST1 | Schaerbeek SIOMAB 1 | SCHAERBEEK SIOMAB ST1 | #N/A | #N/A | #N/A | #N/A | TAMINCO Gent WKK | TAMINCO GENT CHP
SCHAERBEEK SIOMAB ST2 | SCHAERBEEK SIOMAB ST2 | Schaerbeek SIOMAB 2 | SCHAERBEEK SIOMAB ST2 | #N/A | #N/A | #N/A | #N/A | TIHANGE 1N | TIHANGE 1N
SCHAERBEEK SIOMAB ST3 | SCHAERBEEK SIOMAB ST3 | Schaerbeek SIOMAB 3 | SCHAERBEEK SIOMAB ST3 | #N/A | #N/A | #N/A | #N/A | TIHANGE 1S | TIHANGE 1S
Scheldelaan Exxonmobil | Scheldelaan Exxonmobil | SCHELDELAAN EXXONMOBIL | Scheldelaan Exxonmobil | SCHELDELAAN EXXONMOBIL | SCHELDELAAN EXXONMOBIL | SCHELDELAAN EXXONMOBIL | SCHELDELAAN EXXONMOBIL | TIHANGE 3 | Tihange 3
STORA LANGERBRUGGE WKK1 | STORA LANGERBRUGGE WKK1 | STORA LANGERBRUGGE CHP 1 | STORA LANGERBRUGGE WKK1 | #N/A | #N/A | #N/A | #N/A | T-Power | T-POWER
STORA LANGERBRUGGE WKK2 | STORA LANGERBRUGGE WKK2 | STORA LANGERBRUGGE CHP 2 | STORA LANGERBRUGGE WKK2 | #N/A | #N/A | #N/A | #N/A | Vilvoorde GT | VILVOORDE GT
Syral Aalst GT+ST | Syral Aalst GT | AALST SYRAL GT | Syral Aalst GT+ST | #N/A | Syral Aalst GT | AALST SYRAL GT | AALST SYRAL GT | Wilmarsdonk Total GT1 | WILMARSDONK TOTAL GT1
Syral Aalst GT+ST | Syral Aalst ST | AALST SYRAL ST | Syral Aalst GT+ST |  | Syral Aalst ST | AALST SYRAL ST | AALST SYRAL ST | Wilmarsdonk Total GT2 | WILMARSDONK TOTAL GT2
TAMINCO Gent WKK | TAMINCO Gent WKK | TAMINCO GENT CHP | TAMINCO Gent WKK | #N/A | #N/A | #N/A | #N/A | Wilmarsdonk Total GT3 | WILMARSDONK TOTAL GT3
TIHANGE 1N | TIHANGE 1N | TIHANGE 1N | TIHANGE 1N | TIHANGE 1N | TIHANGE 1N | TIHANGE 1N | TIHANGE 1N | Zandvliet Power | ZANDVLIET POWER
TIHANGE 1S | TIHANGE 1S | TIHANGE 1S | TIHANGE 1S | TIHANGE 1S | TIHANGE 1S | TIHANGE 1S | TIHANGE 1S | Zedelgem TJ | ZEDELGEM TJ
TIHANGE 2 | TIHANGE 2 | TIHANGE 2 | TIHANGE 2 | TIHANGE 2 | TIHANGE 2 | #N/A | TIHANGE 2 | Zeebrugge TJ | ZEEBRUGGE TJ
TIHANGE 3 | TIHANGE 3 | Tihange 3 | TIHANGE 3 | Tihange 3 | Tihange 3 | Tihange 3 | Tihange 3 | Zelzate 2 Knippegroen | KNIPPEGROEN STEG
T-Power | T-Power | T-POWER | T-Power | T-POWER | T-POWER | T-POWER | T-POWER | Zelzate TJ | ZELZATE TJ
TURBOJET VOLTA | TURBOJET VOLTA | TURBOJET VOLTA | TURBOJET VOLTA | TURBOJET VOLTA | TURBOJET VOLTA | #N/A | TURBOJET VOLTA | Zwijndrecht Lanxess GT | Zwijndrecht Lanxess GT
Vilvoorde GT | Vilvoorde GT | VILVOORDE GT | Vilvoorde GT | VILVOORDE GT | VILVOORDE GT | VILVOORDE GT | VILVOORDE GT | Zwijndrecht Lanxess ST | Zwijndrecht Lanxess ST
- | Vilvoorde ST | VILVOORDE ST |  | Vilvoorde ST | Vilvoorde ST | VILVOORDE ST | VILVOORDE ST
SERAING_newCCGT | EDF Luminus Seraing NEW | EDF Luminus Seraing NEW | SERAING_newCCGT | #N/A | EDF Luminus Seraing NEW | #N/A | EDF Luminus Seraing NEW
Wilmarsdonk Total GT1 | Wilmarsdonk Total GT1 | WILMARSDONK TOTAL GT1 | Wilmarsdonk Total GT1 | WILMARSDONK TOTAL GT1 | WILMARSDONK TOTAL GT1 | WILMARSDONK TOTAL GT1 | WILMARSDONK TOTAL GT1
Wilmarsdonk Total GT2 | Wilmarsdonk Total GT2 | WILMARSDONK TOTAL GT2 | Wilmarsdonk Total GT2 | WILMARSDONK TOTAL GT2 | WILMARSDONK TOTAL GT2 | WILMARSDONK TOTAL GT2 | WILMARSDONK TOTAL GT2
Wilmarsdonk Total GT3 | Wilmarsdonk Total GT3 | WILMARSDONK TOTAL GT3 | Wilmarsdonk Total GT3 | WILMARSDONK TOTAL GT3 | WILMARSDONK TOTAL GT3 | WILMARSDONK TOTAL GT3 | WILMARSDONK TOTAL GT3
Zandvliet Power | Zandvliet Power | ZANDVLIET POWER | Zandvliet Power | ZANDVLIET POWER | ZANDVLIET POWER | ZANDVLIET POWER | ZANDVLIET POWER
Zandvliet Power Repowering | #N/A | #N/A | Zandvliet Power Repowering | #N/A | #N/A | #N/A | #N/A
Zedelgem TJ | Zedelgem TJ | ZEDELGEM TJ | Zedelgem TJ | ZEDELGEM TJ | ZEDELGEM TJ | ZEDELGEM TJ | ZEDELGEM TJ
Zeebrugge TJ | Zeebrugge TJ | ZEEBRUGGE TJ | Zeebrugge TJ | ZEEBRUGGE TJ | ZEEBRUGGE TJ | ZEEBRUGGE TJ | ZEEBRUGGE TJ
E-wood | E-wood | E-wood | E-wood | E-wood | E-wood | E-wood | E-wood
Borealis Kallo | Borealis Kallo Cogen GT_ST | Borealis Kallo Cogen GT_ST | Borealis Kallo | #N/A | Borealis Kallo Cogen GT_ST | Borealis Kallo Cogen GT_ST | Borealis Kallo Cogen GT_ST
EDF Luminus Seraing ST | EDF Luminus Seraing ST | EDF Luminus Seraing ST | EDF Luminus Seraing ST | EDF Luminus Seraing ST | EDF Luminus Seraing ST | #N/A | EDF Luminus Seraing ST
TIHANGE 3_EXT | #N/A | #N/A | TIHANGE 3_EXT | #N/A | #N/A | #N/A | #N/A
DOEL 4_EXT | #N/A | #N/A | DOEL 4_EXT | #N/A | #N/A | #N/A | #N/A

## 1.2. Renewable & decentralised
1.2. Renewable energy sources and decentralised thermal production
This section concerns renewable energy sources (e.g. wind and solar photovoltaics) as well as decentralised thermal generation (i.e. smaller CHP units, biomass and waste units). Please refer to the online published study report for more information on the methodology and assumptions.
Generation capacity at the end of the mentioned year [MW]
Generation type |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Wind |  | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2960 | 5760 | 5760 | 5760 | 5760 | 5760
| Wind onshore |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wind offshore |  | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2261 | 2960 | 5760 | 5760 | 5760 | 5760 | 5760
| Photovoltaics |  | 7450 | 8330 | 9210 | 10090 | 10970 | 11850 | 12730 | 13610 | 14490 | 15370 | 16250 | 17130 | 18010
| Hydro RoR |  | 125 | 129 | 133 | 137 | 140 | 143 | 145 | 148 | 151 | 154 | 157 | 160 | 163
| Gas CHP - decentralised |  | 1484 | 1499 | 1499 | 1499 | 1546.5 | 1594 | 1594 | 1594 | 1594 | 1594 | 1594 | 1594 | 1594
| Turbines |  | 979 | 982 | 982 | 982 | 988 | 995 | 995 | 995 | 995 | 995 | 995 | 995 | 995
| Motors |  | 505 | 517 | 517 | 517 | 558 | 599 | 599 | 599 | 599 | 599 | 599 | 599 | 599
| Biomass - decentralised |  | 547 | 547 | 547 | 547 | 557 | 567 | 567 | 567 | 567 | 567 | 567 | 567 | 567
| Waste - decentralised |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
Photovoltaics | The solar photovoltaics capacity in Belgium is assumed to grow by 880 MWp per year.
[17 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
[16 empty] | Historic (IEA) | 2010: 1007; 2011: 1979; 2012: 2647; 2013: 2902; 2014: 3014; 2015: 3131; 2016: 3330; 2017: 3620; 2018: 4000; 2019: 4640; 2020: 5570; 2021: 6580
[16 empty] | NECP2019_WAM | 2025: 8000; 2030: 11000
[16 empty] | AdeqFlex'21 | 2022: 6352; 2023: 6902; 2024: 7451; 2025: 8000; 2026: 8600; 2027: 9200; 2028: 9800; 2029: 10400; 2030: 11000; 2031: 11600; 2032: 12200
[16 empty] | AdeqFlex'23 | 2021: 6580; 2022: 7450; 2023: 8330; 2024: 9210; 2025: 10090; 2026: 10970; 2027: 11850; 2028: 12730; 2029: 13610; 2030: 14490; 2031: 15370; 2032: 16250; 2033: 17130; 2034: 18010
Wind onshore | The onshore wind capacity in Belgium is assumed to grow by 330 MW per year.
[17 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
[16 empty] | Historic (IEA) | 2010: 716; 2011: 873; 2012: 989; 2013: 1072; 2014: 1236; 2015: 1464; 2016: 1658; 2017: 1915; 2018: 2130; 2019: 2320; 2020: 2471; 2021: 2726
[16 empty] | NECP2019_WAM | 2025: 3747; 2030: 4900
[16 empty] | AdeqFlex'21 | 2022: 2981.42; 2023: 3236.63; 2024: 3491.84; 2025: 3747; 2026: 3978; 2027: 4208; 2028: 4439; 2029: 4669; 2030: 4900; 2031: 5131; 2032: 5362
[16 empty] | AdeqFlex'23 | 2021: 2726; 2022: 2938; 2023: 3268; 2024: 3598; 2025: 3928; 2026: 4258; 2027: 4588; 2028: 4918; 2029: 5248; 2030: 5578; 2031: 5908; 2032: 6238; 2033: 6568; 2034: 6898
Wind offshore | The assumed capacity in offshore wind capacity in Belgium follows the latest planning of the Princess Elisabeth Zone capacity.
[17 empty] | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
[16 empty] | Historic (IEA) | 2010: 200; 2011: 200; 2012: 400; 2013: 400; 2014: 700; 2015: 700; 2016: 700; 2017: 900; 2018: 1100; 2019: 1570; 2020: 2261; 2021: 2261
NECP2019_WAM
[16 empty] | AdeqFlex'21 | 2022: 2253; 2023: 2253; 2024: 2253; 2025: 2253; 2026: 2953; 2027: 2953; 2028: 4000; 2029: 4000; 2030: 4000; 2031: 4000; 2032: 4000
[16 empty] | AdeqFlex'23 | 2021: 2261; 2022: 2261; 2023: 2261; 2024: 2261; 2025: 2261; 2026: 2261; 2027: 2261; 2028: 2261; 2029: 2960; 2030: 5760; 2031: 5760; 2032: 5760; 2033: 5760; 2034: 5760
Hydro RoR | This category covers the hydro Run Of River capacity assumed in Belgium. Belgium has limited capacity in terms of run-of-river hydro-electricity.Those consist of small hydro units (installed along rivers) with the ‘biggest’ ones on the river Meuse.
[28 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
[16 empty] | Hydro ROR | [11 empty] | 121 | 125 | 129 | 133 | 137 | 140 | 143 | 145 | 148 | 151 | 154 | 157 | 160 | 163
Decentralised Biomass, Waste, CHP | In this category, smaller decentralised production units, usually connected to the distribution grid (DSO) are considered. A database covering those projects is maintained by Elia and updated on monthly basis by exchanges with DSO and grid users. This also includes new projects that are being developped.
[28 empty] | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
[16 empty] | Waste | [12 empty] | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
[16 empty] | Biomass | [12 empty] | 547 | 547 | 547 | 547 | 557 | 567 | 567 | 567 | 567 | 567 | 567 | 567 | 567
[16 empty] | CHP | [12 empty] | 1484 | 1499 | 1499 | 1499 | 1546.5 | 1594 | 1594 | 1594 | 1594 | 1594 | 1594 | 1594 | 1594

## 2.1. Tot. elec. demand charts (hidden)
2.1. Total electricity consumption
The total electricity demand for Belgium is based on the tool developped by Climact and used in the previous Adequacy & Flexibility study (2021), where the methodology used is described in the following report:
https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2020/20200603_total-electricity-demand-forecasting_en.pdf
It includes the forecasted total electricity demand which is build up based on several elements:
1) It includes the impact of macro-economic forecasts based on the report published by the Federal Plan Bureau:
Bureau fédéral du Plan - Publication - Perspectives économiques 2022-2027 – Version de juin 2022
2) It includes the trends in terms of electrification of transport & heating
cfr. Section 2.1.1 & 2.1.2
3) it includes the impact of high prices as presented in the WG Adequacy on 25/08/2022
This forecast does not include additional electricity demand which might occur in the industrial sector and/or the growth of new industries (mainly data centers)
A range is proposed to capture this additional electrification
cfr. Section 2.1.3
Range proposed on Public consultation 28/10
TWh | Year | Historical normalised total demand | Organic total demand | Total Demand incl. EV & HP | Min Range | Max Range | Total demand Best Estimate | Total demand industry rebound | Min Range increase | Max Range increase
historical | 2010 | 89.3 | 89.3
historical | 2011 | 88.2 | 88.2
historical | 2012 | 84.7 | 84.7
historical | 2013 | 85.8 | 85.8
historical | 2014 | 89.4 | 89.4
historical | 2015 | 88.3 | 88.3
historical | 2016 | 86.4 | 86.4
historical | 2017 | 87.4 | 87.4
historical | 2018 | 88 | 88
historical | 2019 | 85.7 | 85.7
historical | 2020 | 82.1 | 82.1
historical | 2021 | 84.7 | 84.7 | [5 empty] | 0
historical | 2022 | 82.9 | 82.9 | 82.9 | 83.6 | 83.6 | 82.9 | 82.9 | 0.7 | 0
| 2023 |  | 81.3 | 82.1 | 84 | 85.3 | 82.6 | 84.8 | 2.7 | 1.3
| 2024 |  | 81.8 | 83.2 | 85.8 | 88.2 | 84.5 | 87.3 | 4 | 2.4
| 2025 |  | 83 | 85.6 | 87.6 | 91.9 | 88.7 | 90.8 | 4.6 | 4.3
| 2026 |  | 85.5 | 89.5 | 89.2 | 96.2 | 95.7 | 95.7 | 3.7 | 7
| 2027 |  | 86 | 91.4 | 91.7 | 101.7 | 99.7 | 99.7 | 5.7 | 10
| 2028 |  | 86.4 | 93.2 | 96 | 107.3 | 104.4 | 104.4 | 9.6 | 11.3
| 2029 |  | 86.8 | 95 | 102 | 113.1 | 108.3 | 108.3 | 15.2 | 11.1
| 2030 |  | 87.3 | 96.7 | 107.4 | 118.5 | 112.1 | 112.1 | 20.1 | 11.1
| 2031 |  | 87.7 | 98.4 | 111.1 | 122.8 | 116.4 | 116.4 | 23.4 | 11.7
| 2032 |  | 88.2 | 100.1 | 114.4 | 127.1 | 120.6 | 120.6 | 26.2 | 12.7
| 2033 |  | 88.6 | 101.8 | 117.3 | 131.4 | 124.8 | 124.8 | 28.7 | 14.1
| 2034 |  | 88.9 | 103.5 | 120 | 135.7 | 128.5 | 128.5 | 31.1 | 15.7
| 2035 |  | 89 | 105 | 123 | 139.8 | 132.3 | 132.3 | 34 | 16.8
2.1.1. Electrification of the transport sector
Passenger cars
| Unit | Value | Source |  | Key Drivers
Usage - private | km/year | 22750.4363 | Derived from global average car usage and relative relation company/private ~ FEBIAC |  | Passenger car sales continue the trend of 2020-2022 with reduced sales mainly in the private car segment (1)
Usage - private | km/year | 12348.1517 | Derived from global average car usage and relative relation company/private ~ FEBIAC |  | All regions reach 100% BEV car sales by 2035 due to EU-wide ban on new ICE (2)
Consumption - BEV | kWh/100km | 18 | Several sources |  | Company cars: 100% BEV sales in all regions by 2029 due to federal fiscal measures & BXL LEZ (3)(5)
Consumption - PHEV company | kWh/100km | 2.34 | theicct.org (6) |  | FL: region reaches 100% BEV sales by 2029 for private cars (4)
Consumption - PHEV private | kWh/100km | 8.46 | theicct.org (6) |  | BXL: no more gasoline & diesel respectively 2030, 2035 due to LEZ (5)
Sales - company | thousand units/y) | 235 | Febiac 2020-2021 |  | A distinction is made in the mileage of cars in the company/private segment (1)
Sales - private | thousand units/y) | 180 | Febiac 2020-2021 |  | A distinction is made in the usage of PHEV cars in the company/private segment (6)
Sources used
[5 empty] | BE | (1) Datadigest 2021 (febiac.be)
[5 empty] | EU | (2) Fit for 55: MEPs back objective of zero emissions for cars and vans in 2035 ¦ News ¦ European Parliament (europa.eu)
[5 empty] | BE | (3) Minister Van Peteghem maakt van bedrijfswagens en laadpalen de hefbomen naar een groener wagenpark ¦ Vincent Van Peteghem (belgium.be)
[5 empty] | FL | (4) VR 2021 0511 DOC.1237-1 Visienota VEKP Bijkomende maatregelen.pdf (energiesparen.be)
“B.2 Uitfasering aankoop fossiele verbrandingsmotoren ”
[5 empty] | BXL | (5) Praktisch pagina ¦ Low Emission Zone (lez.brussels)
[5 empty] | Usage PHEV | (6) Real-world usage of plug-in hybrid vehicles in Europe: A 2022 update on fuel consumption, electric driving, and CO2 emissions - International Council on Clean Transportation (theicct.org)
|  |  | Company |  | Private |  | LDV |  | HDV | Bus | [6 empty] | Equivalent Units (PHEV counted based on their electric mode)
Million units | Year |  | BEV | PHEV | BEV | PHEV | BEV | PHEV | BEV | BEV | [5 empty] | Year | Passenger car | LDV | HDV+bus | HDV | Bus | Total | Company equivalent | Private Equivalent | equivalent % of stock
| 2021 |  | 0.05 | 0.11 | 0 | 0.01 | 0.00312 | 0.00078 | 1.8e-05 | 0.00047 | [5 empty] | 2021 | 0.069 | 0.00351 | 0.000488 | 1.8e-05 | 0.00047 | 0.072998 | 0.0643 | 0.0047 | 1.2%
| 2022 |  | 0.08 | 0.16 | 0.01 | 0.02 | 0.00619 | 0.00205 | 3.1919e-05 | 0.00091 | [5 empty] | 2022 | 0.1202 | 0.00721 | 0.00094192 | 3.1919e-05 | 0.00091 | 0.12835 | 0.1008 | 0.0194 | 2.1%
| 2023 |  | 0.13 | 0.23 | 0.02 | 0.04 | 0.01075 | 0.00403 | 5.3835e-05 | 0.00136 | [5 empty] | 2023 | 0.1987 | 0.01277 | 0.0014138 | 5.3835e-05 | 0.00136 | 0.21288 | 0.1599 | 0.0388 | 3.3%
| 2024 |  | 0.2 | 0.3 | 0.03 | 0.06 | 0.01765 | 0.00685 | 8.942e-05 | 0.0018 | [5 empty] | 2024 | 0.2972 | 0.02107 | 0.0018894 | 8.942e-05 | 0.0018 | 0.32016 | 0.239 | 0.0582 | 5.3%
| 2025 |  | 0.34 | 0.35 | 0.06 | 0.08 | 0.02794 | 0.01048 | 0.00014729 | 0.00224 | [5 empty] | 2025 | 0.4831 | 0.03317 | 0.0023873 | 0.00014729 | 0.00224 | 0.51866 | 0.3855 | 0.0976 | 8.6%
| 2026 |  | 0.54 | 0.34 | 0.11 | 0.1 | 0.04283 | 0.01469 | 0.00024347 | 0.00268 | [5 empty] | 2026 | 0.7412 | 0.05018 | 0.0029235 | 0.00024347 | 0.00268 | 0.7943 | 0.5842 | 0.157 | 13.3%
| 2027 |  | 0.72 | 0.31 | 0.18 | 0.12 | 0.06343 | 0.01923 | 0.00040113 | 0.00312 | [5 empty] | 2027 | 0.9967 | 0.07305 | 0.0035211 | 0.00040113 | 0.00312 | 1.0733 | 0.7603 | 0.2364 | 17.8%
| 2028 |  | 0.89 | 0.26 | 0.28 | 0.14 | 0.09029 | 0.02386 | 0.00079051 | 0.00356 | [5 empty] | 2028 | 1.2696 | 0.10222 | 0.0043505 | 0.00079051 | 0.00356 | 1.3762 | 0.9238 | 0.3458 | 22.8%
| 2029 |  | 1.02 | 0.21 | 0.4 | 0.14 | 0.12309 | 0.02843 | 0.0021197 | 0.004 | [5 empty] | 2029 | 1.5131 | 0.1373 | 0.0061197 | 0.0021197 | 0.004 | 1.6565 | 1.0473 | 0.4658 | 27.3%
| 2030 |  | 1.08 | 0.15 | 0.53 | 0.14 | 0.1607 | 0.03294 | 0.0044658 | 0.00444 | [5 empty] | 2030 | 1.6953 | 0.17717 | 0.0089058 | 0.0044658 | 0.00444 | 1.8814 | 1.0995 | 0.5958 | 30.6%
| 2031 |  | 1.13 | 0.11 | 0.66 | 0.14 | 0.20156 | 0.03605 | 0.0074344 | 0.00562 | [5 empty] | 2031 | 1.8701 | 0.21958 | 0.013054 | 0.0074344 | 0.00562 | 2.1027 | 1.1443 | 0.7258 | 33.9%
| 2032 |  | 1.16 | 0.07 | 0.81 | 0.14 | 0.24407 | 0.03775 | 0.011022 | 0.00681 | [5 empty] | 2032 | 2.0449 | 0.26295 | 0.017832 | 0.011022 | 0.00681 | 2.3257 | 1.1691 | 0.8758 | 37.3%
| 2033 |  | 1.19 | 0.04 | 0.96 | 0.13 | 0.28695 | 0.03814 | 0.015215 | 0.00799 | [5 empty] | 2033 | 2.2163 | 0.30602 | 0.023205 | 0.015215 | 0.00799 | 2.5455 | 1.1952 | 1.0211 | 40.7%
| 2034 |  | 1.22 | 0.02 | 1.12 | 0.13 | 0.32928 | 0.03757 | 0.019959 | 0.00917 | [5 empty] | 2034 | 2.4037 | 0.34806 | 0.029129 | 0.019959 | 0.00917 | 2.7809 | 1.2226 | 1.1811 | 44.2%
| 2035 |  | 1.24 | 0 | 1.28 | 0.12 | 0.37181 | 0.03554 | 0.025195 | 0.01036 | [5 empty] | 2035 | 2.5764 | 0.38958 | 0.035555 | 0.025195 | 0.01036 | 3.0015 | 1.24 | 1.3364 | 47.6%
LDV freight (Vans)
| Value | Source |  | Key Drivers
Usage (km/year) | 16 500 | Febiac: total km/#units |  | Sales slightly below historical 10y average (+/- 65k/y) (1)
Efficiency (kWh/100km) - BEV | 30 | Several sources |  | Electrification of Vans follows the passenger car segment, but with a delayed uptake.
Efficiency (kWh/100km) - PHEV | 15 | Several sources |  | Main driver being the ICE ban also applicable for vans from 2035, sucht that 100% BEV sales are reached in 2035 (2)
Sales (thousand units/y) | 60 | Febiac 10y avg & slightly reduced |  | Sources used
|  |  |  | BE | (1) Datadigest 2021 (febiac.be)
|  |  |  | EU | (2) Fit for 55: MEPs back objective of zero emissions for cars and vans in 2035 ¦ News ¦ European Parliament (europa.eu)
thousands units | Year |  | BEV | PHEV | Equivalent Units (PHEV counted as 1/2) | equivalent % of stock
| 2021 |  | 3.12 | 0.78 | 3.51 | 0%
| 2022 |  | 6.19 | 2.05 | 7.21 | 1%
| 2023 |  | 10.75 | 4.03 | 12.77 | 1%
| 2024 |  | 17.65 | 6.85 | 21.07 | 2%
| 2025 |  | 27.94 | 10.48 | 33.17 | 4%
| 2026 |  | 42.83 | 14.69 | 50.18 | 6%
| 2027 |  | 63.43 | 19.23 | 73.05 | 8%
| 2028 |  | 90.29 | 23.86 | 102.22 | 11%
| 2029 |  | 123.09 | 28.43 | 137.3 | 15%
| 2030 |  | 160.7 | 32.94 | 177.17 | 19%
| 2031 |  | 201.56 | 36.05 | 219.58 | 23%
| 2032 |  | 244.07 | 37.75 | 262.95 | 28%
| 2033 |  | 286.95 | 38.14 | 306.02 | 32%
| 2034 |  | 329.28 | 37.57 | 348.06 | 36%
| 2035 |  | 371.81 | 35.54 | 389.58 | 40%
HDV freight (Trucks)
| Value | Source |  | Key Drivers
Usage (km/year) | 55 000 | Febiac: total km/#units |  | Sales slightly below historical 10y average (+/-9k/y)
Efficiency (kWh/100km) | 120 | Several sources |  | Very conservative assumptions on electrication with delayed uptake of BEV sales reaching 7% in 2030 and 20% in 2035 (1)
Sales (thousand units/y) | 8 | Febiac 10y avg & slightly reduced
Sources used
|  |  |  | BE | (1) Datadigest 2021 (febiac.be)
|  |  |  | BE | Febiac estimates ~ 20% market share for e-trucks in 2030 (based on bilateral meetring Elia-FEBIAC)
|  |  |  | EU | Electric mobility: TRATON GROUP boosts investment ¦ TRATON
|  |  |  | EU | Mercedes-Benz All eActros LongHaul: In Pictures ¦ Trucks.cardekho.com
|  |  |  | EU | The future of electromobility ¦ Volvo Trucks
|  |  |  | FL | VR 2021 0511 DOC.1237-1 Visienota VEKP Bijkomende maatregelen.pdf (energiesparen.be)
“C.7 Aanmoediging emissievrij vrachtvervoer door gunstig belastingsregime”
“C.9 Versnelde transitie naar zero-emissie vrachtvervoer over de weg”
thousands units | Year |  |  |  | BEV | equivalent % of stock
| 2021 |  |  |  | 0.018 | 0%
| 2022 |  |  |  | 0.031919 | 0%
| 2023 |  |  |  | 0.053835 | 0%
| 2024 |  |  |  | 0.08942 | 0.1%
| 2025 |  |  |  | 0.14729 | 0.1%
| 2026 |  |  |  | 0.24347 | 0.2%
| 2027 |  |  |  | 0.40113 | 0.3%
| 2028 |  |  |  | 0.79051 | 0.5%
| 2029 |  |  |  | 2.1197 | 1.5%
| 2030 |  |  |  | 4.4658 | 3.1%
| 2031 |  |  |  | 7.4344 | 5.2%
| 2032 |  |  |  | 11.0217 | 7.7%
| 2033 |  |  |  | 15.2145 | 10.6%
| 2034 |  |  |  | 19.9586 | 13.9%
| 2035 |  |  |  | 25.1951 | 17.5%
Busses
| Value | Source |  | Key Drivers
Usage (km/year) | 45 000 | Febiac: total km/#units |  | Pledges & ambitions by public bus companies are the key driver for this segment
Efficiency (kWh/100km) | 125 | Several sources |  | FL: De Lijn to reach 100% BEV by 2035
BXL: MIVB to reach 100% BEV by 2030
Sources used
|  |  |  | FL | E-bussen: De Lijn gaat volop voor groen - De Lijn
|  |  |  | BXL | 100% elektrische busvloot tegen 2030 - Pascal Smet
thousands units | Year |  | BEV | PHEV | Equivalent Units (PHEV counted as 1/2) | equivalent % of stock
| 2021 |  | 0.47 | 0 | 0.47 | 2.9%
| 2022 |  | 0.91 | 0 | 0.91 | 5.6%
| 2023 |  | 1.36 | 0 | 1.36 | 8.3%
| 2024 |  | 1.8 | 0 | 1.8 | 11.1%
| 2025 |  | 2.24 | 0 | 2.24 | 13.9%
| 2026 |  | 2.68 | 0 | 2.68 | 16.8%
| 2027 |  | 3.12 | 0 | 3.12 | 19.7%
| 2028 |  | 3.56 | 0 | 3.56 | 22.7%
| 2029 |  | 4 | 0 | 4 | 25.7%
| 2030 |  | 4.44 | 0 | 4.44 | 28.7%
| 2031 |  | 5.62 | 0 | 5.62 | 36.7%
| 2032 |  | 6.81 | 0 | 6.81 | 44.8%
| 2033 |  | 7.99 | 0 | 7.99 | 53.1%
| 2034 |  | 9.17 | 0 | 9.17 | 61.5%
| 2035 |  | 10.36 | 0 | 10.36 | 70%
2.1.2. Electrification of the heating sector
Residential
| Unit | Value | Source |  | Key Drivers
New buildings | thousand/y | 55 | Statbel: avg last 5 years |  | Business as usual in the evolution of new buildings (1)
Renovation rate avg 2022-2035 | % | 1% | assumption |  | Renovations increasing from 0.7% (1) towards 1.3% in 2035
Average Heating demand - new build | kWh/y | 4400 | Fluvius - EPC A |  | FL: no more gas connections from 2025: 96% HP, 4% District heating (2)
Average Heating demand - renovated building | kWh/y | 8000 | Fluvius - EPC C |  | Other regions: 100% HP/DH in new built from 2035
Heat supplied by secondary heater | % | 50% | Assumption after discussion with heat federations |  | Renovations & end-of-lifetime boiler replacement: 15% , 20% HP by 2030, 2035
Average Hot water demand | kWh/y | 1800 | Fluvius |  | Sources used
[5 empty] | BE | Bouwvergunningen ¦ Statbel (fgov.be) (1)
[5 empty] | FL | Verplichting elektrische warmtepomp bij nieuwbouw vervroegd naar 2025 - Ode (2)
Current sales & stock
[5 empty] | BE | ATTB, FRIXIS, Delta-EE, EHPA, Statista, EurObserv'ER, Fluvius
[5 empty] | FL | VEKA: https://apps.energiesparen.be/energiekaart/vlaanderen/warmtepompen-aantal rapp-2021-18.pdf (vreg.be)
[5 empty] | WL | bilan-domestique-et-equivalents-2019-v2.pdf (wallonie.be) p29
|  |  | Residential |  |  |  | Tertiary |  |  |  | Residential & Tertiary
thousands units | Year |  | AA HP | AW HP | GW HP | AA HP (secondary)* | AA HP | AW HP | GW HP | AA HP (secondary)* | AA HP | AW HP | GW HP | AA HP (secondary)* | total |  |  |  |  | Total | equivalent % of stock
| 2021 |  | 87 | 71 | 21 | 330 | 6 | 2 | 1 | 22 | 0.093 | 0.073 | 0.022 | 0.352 | 0.54 |  |  |  |  | 509 | 8.41%
| 2022 |  | 111 | 92 | 27 | 419 | 7 | 3 | 1 | 28 | 0.118 | 0.095 | 0.028 | 0.447 | 0.688 |  |  |  |  | 648 | 10.45%
| 2023 |  | 115 | 114 | 32 | 428 | 8 | 7 | 2 | 30 | 0.123 | 0.121 | 0.034 | 0.458 | 0.736 |  |  |  |  | 690 | 11.05%
| 2024 |  | 121 | 144 | 39 | 439 | 9 | 13 | 3 | 33 | 0.13 | 0.157 | 0.042 | 0.472 | 0.801 |  |  |  |  | 743 | 11.83%
| 2025 |  | 128 | 188 | 49 | 450 | 10 | 19 | 5 | 36 | 0.138 | 0.207 | 0.054 | 0.486 | 0.885 |  |  |  |  | 815 | 12.91%
| 2026 |  | 135 | 234 | 60 | 463 | 11 | 26 | 6 | 40 | 0.146 | 0.26 | 0.066 | 0.503 | 0.975 |  |  |  |  | 893 | 14.06%
| 2027 |  | 144 | 283 | 71 | 478 | 12 | 33 | 8 | 45 | 0.156 | 0.316 | 0.079 | 0.523 | 1.074 |  |  |  |  | 975 | 15.26%
| 2028 |  | 153 | 333 | 82 | 493 | 14 | 41 | 9 | 50 | 0.167 | 0.374 | 0.091 | 0.543 | 1.175 |  |  |  |  | 1061 | 16.51%
| 2029 |  | 164 | 385 | 93 | 510 | 16 | 50 | 11 | 55 | 0.18 | 0.435 | 0.104 | 0.565 | 1.284 |  |  |  |  | 1152 | 17.82%
| 2030 |  | 175 | 439 | 105 | 528 | 18 | 58 | 12 | 59 | 0.193 | 0.497 | 0.117 | 0.587 | 1.394 |  |  |  |  | 1248 | 19.19%
| 2031 |  | 188 | 496 | 117 | 548 | 20 | 67 | 14 | 64 | 0.208 | 0.563 | 0.131 | 0.612 | 1.514 |  |  |  |  | 1348 | 20.62%
| 2032 |  | 201 | 554 | 129 | 569 | 22 | 76 | 16 | 68 | 0.223 | 0.63 | 0.145 | 0.637 | 1.635 |  |  |  |  | 1454 | 22.11%
| 2033 |  | 216 | 615 | 141 | 592 | 24 | 84 | 18 | 73 | 0.24 | 0.699 | 0.159 | 0.665 | 1.763 |  |  |  |  | 1564 | 23.65%
| 2034 |  | 232 | 679 | 154 | 616 | 26 | 94 | 20 | 76 | 0.258 | 0.773 | 0.174 | 0.692 | 1.897 |  |  |  |  | 1680 | 25.25%
| 2035 |  | 248 | 744 | 167 | 641 | 28 | 103 | 22 | 80 | 0.276 | 0.847 | 0.189 | 0.721 | 2.033 |  |  |  |  | 1801 | 26.91%
* Included in this category are Air-Air reversible heat pumps which have seen a sharp increase in recent years. These units are typically installed as an AC (cooling) unit but also have the capability to deliver heat, albeit in general limited to a part of the building and/or as a secondary form of heating
After consultation with ATTB, FRIXIS and contacts within the heat pump sector, it was decided to categorise these A-A (reversible) units for 80% in the hybrid category as they will have different characteristics when it comes to yearly and hourly electricity demand
Tertiary
| Unit | Value | Source |  | Key Drivers
New buildings | thousand/y | 5.8 | Statbel: avg last 5 years |  | Business as usual in the evolution of new buildings (1)
Renovation rate avg 2022-2035 | % | 1% | assumption |  | Renovations increasing from 0.7% (1) towards 1.3% in 2035
Average Heating demand - new build | kWh/y | 17000 | Average building consumption & 50% new built reduction |  | In general: faster uptake of Heat pumps as compared to residential sector
Average Heating demand - renovated building | kWh/y | 25500 | Average building consumption & 25% renovation reduction |  | FL: no more gas connections from 2025: 96% HP, 4% District heating (2)
Average Hot water demand | kWh/y | 3600 | Double the amount of residential |  | Renovations: 100% HP by 2030
End-of-lifetime boiler replacement: 25% , 35% HP by 2030, 2035
Sources used
[5 empty] | BE | Bouwvergunningen ¦ Statbel (fgov.be) (1)
[5 empty] | FL | Verplichting elektrische warmtepomp bij nieuwbouw vervroegd naar 2025 - Ode (2)
Current sales & stock
[5 empty] | BE | ATTB, FRIXIS, Delta-EE, EHPA, Statista, EurObserv'ER
[5 empty] | FL | VEKA: https://apps.energiesparen.be/energiekaart/vlaanderen/warmtepompen-aantal rapp-2021-18.pdf (vreg.be)
Verplichtingen voor niet-residentiële gebouwen ¦ Vlaanderen.be
[5 empty] | WL | bilan-domestique-et-equivalents-2019-v2.pdf (wallonie.be) p29
thousands units | Year |  | AA HP | AW HP | GW HP | AA HP (secondary)* | Total | equivalent % of stock
| 2021 |  | 6 | 2 | 1 | 22 | 31 | 3.9%
| 2022 |  | 7 | 3 | 1 | 28 | 39 | 4.9%
| 2023 |  | 8 | 7 | 2 | 30 | 47 | 6.1%
| 2024 |  | 9 | 13 | 3 | 33 | 58 | 7.5%
| 2025 |  | 10 | 19 | 5 | 36 | 70 | 9%
| 2026 |  | 11 | 26 | 6 | 40 | 83 | 10.7%
| 2027 |  | 12 | 33 | 8 | 45 | 98 | 12.6%
| 2028 |  | 14 | 41 | 9 | 50 | 114 | 14.7%
| 2029 |  | 16 | 50 | 11 | 55 | 132 | 17%
| 2030 |  | 18 | 58 | 12 | 59 | 147 | 19.2%
| 2031 |  | 20 | 67 | 14 | 64 | 165 | 21.4%
| 2032 |  | 22 | 76 | 16 | 68 | 182 | 23.7%
| 2033 |  | 24 | 84 | 18 | 73 | 199 | 26%
| 2034 |  | 26 | 94 | 20 | 76 | 216 | 28.3%
| 2035 |  | 28 | 103 | 22 | 80 | 233 | 30.7%
2.1.3. Additional electrification in industry & data centers
Key Drivers
Published a viewpoint specifically industry, logistics and data centers on 18/11/2022
This study includes quantified trajectories for industrial demand up to 2050 as well as intermediate values for 2030 & 2040
The forecast for 2030 is based on real-life observed requests from Elia-connected clients and in depth consultation with different industrial companies, sectoral organisations and researchers
These connection requests do not all translate into real-life projects, therefore a range was proposed during the public consultation where:
The lower range represents electricity demand increase due to projects that have been confirmed
The higher range represents electricity demand increase due to projects that have been confirmed + requests which are net yet completely certain
Based on this range a final trajectory is now proposed taking as much as possible real connection dates of industrial consumers into account
Flexibility
It must be noted that a significant share of this additional electricity demand is focused on the electrification of heat (electric steam boiler, industrial heat pumps, electric ovens…) & other types of flexible demand
Therefore, not all of this demand will result in additional peak demand and will likely be able to deliver flexibility services, assumptions are included in XXX
Additional electrification in industry
Range
TWh | Year |  | Industry - Low | Industry - High | Final Trajectory
| 2021 |  | 0 | 0 |  | 0
| 2022 |  | 0 | 0 |  | 0
| 2023 |  | 0 | 1.1 | 0.3 | 1.1
| 2024 |  | 0 | 2.1 | 0.6 | 2.1
| 2025 |  | 0 | 3.8 | 2.3 | 3.8
| 2026 |  | 0.1 | 6.3 | 4.9 | 6.2
| 2027 |  | 0.4 | 9.5 | 6.6 | 9.1
| 2028 |  | 2.4 | 12.8 | 9.2 | 10.4
| 2029 |  | 6 | 16 | 10.9 | 10
| 2030 |  | 9 | 19.1 | 12.7 | 10.1
| 2031 |  | 10.6 | 21.2 | 14.9 | 10.6
| 2032 |  | 11.9 | 23.2 | 17 | 11.3
| 2033 |  | 12.8 | 25.3 | 19 | 12.5
| 2034 |  | 13.4 | 27.3 | 20.6 | 13.9
| 2035 |  | 14.5 | 29.4 | 22.3 | 14.9
*This excludes additional electricity demand from electrolyzers & other PtX processes
Additional electrification due to data centers
Key Drivers
The values for the short time frame are based on confirmed connection volumes and dates known by Elia
The forecast towards 2030 and beyond is also based on real-life observed requests from Elia-connected clients and in depth consultation with different market parties
An estimation is made on how likely those projects are to come to existence
Range
TWh | Year |  | Data Center - Low | Data Center - High | Final Trajectory
| 2021 |  | 0 | 0 |  | 0
| 2022 |  | 0 | 0 |  | 0
| 2023 |  | 0 | 0.2 | 0.1 | 0.2
| 2024 |  | 0 | 0.3 | 0.7 | 0.3
| 2025 |  | 0.1 | 0.6 | 0.8 | 0.5
| 2026 |  | 0.2 | 1 | 1.3 | 0.8
| 2027 |  | 0.5 | 1.5 | 1.7 | 1
| 2028 |  | 1 | 2 | 2 | 1
| 2029 |  | 1.5 | 2.5 | 2.4 | 1
| 2030 |  | 2 | 3 | 2.7 | 1
| 2031 |  | 2.4 | 3.6 | 3.1 | 1.2
| 2032 |  | 2.8 | 4.2 | 3.5 | 1.4
| 2033 |  | 3.2 | 4.8 | 3.9 | 1.6
| 2034 |  | 3.6 | 5.4 | 4.4 | 1.8
| 2035 |  | 4 | 6 | 5 | 2
Passenger car
Light duty Vehicle
e-truck & bus
Passenger company car
Light duty Vehicle
e-truck & bus
Passenger private car
Air-Air HP
Air-Water HP
Ground-Water HP
Air-Air HP as secondary heating

## 2.1. Tot. elec. demand
2.1. Total electricity consumption
This section concerns the assumed total electricity demand which is build up based on several elements:
- existing usages of electricity
- electrification of heat (Heat Pumps) and transport (Electric Vehicles)
- new forms of electrification in industry (power-to-heat, CCS, DRI-EAF, data centres, electrolysers..)
- grid losses
Please refer to the online published study report for details regarding methodology, assumptions and sources.
TWh | Year | Historical normalised total demand | Exising usages | Losses | Additional HP | Additional EV | Net other industry** | Data centres | CCS | DRI-EAF | Power-to-heat* | New electrolysers* | Assumed total demand - CENTRAL
historical | 2010 | 89.3 | 85 | 4.3
historical | 2011 | 88.2 | 84.1 | 4.2
historical | 2012 | 84.7 | 80.6 | 4.1
historical | 2013 | 85.8 | 81.8 | 4
historical | 2014 | 89.4 | 85.6 | 3.8
historical | 2015 | 88.3 | 84.5 | 3.8
historical | 2016 | 86.4 | 82.6 | 3.8
historical | 2017 | 87.4 | 83.6 | 3.8
historical | 2018 | 88 | 84.2 | 3.8
historical | 2019 | 85.7 | 81.9 | 3.8
historical | 2020 | 82.1 | 78.3 | 3.8
historical | 2021 | 84.7 | 81.1 | 3.6
historical | 2022 | 82.9 | 79.4 | 3.5 | [8 empty] | 82.9
| 2023 |  | 77.9 | 3.7 | 0.1 | 0.3 | 0.1 | 0.1 | 0 | 0 | 0.3 | 0 | 82.6
| 2024 |  | 78.3 | 3.8 | 0.3 | 0.8 | 0.2 | 0.7 | 0 | 0 | 0.4 | 0 | 84.5
| 2025 |  | 79.6 | 4 | 0.5 | 1.6 | 0.6 | 0.8 | 0.4 | 0 | 1 | 0 | 88.4
| 2026 |  | 82 | 4.1 | 0.8 | 2.6 | -0.3 | 1.3 | 0.7 | 2.6 | 1.7 | 0.1 | 95.5
| 2027 |  | 82.4 | 4.3 | 1 | 3.7 | -0.1 | 1.7 | 1.1 | 2.6 | 2.7 | 0.1 | 99.5
| 2028 |  | 82.6 | 4.5 | 1.3 | 4.8 | 0.2 | 2.1 | 2.1 | 2.6 | 3.9 | 0.2 | 104.2
| 2029 |  | 83 | 4.7 | 1.6 | 5.8 | 0.7 | 2.4 | 2.1 | 2.6 | 5.3 | 0.4 | 108.6
| 2030 |  | 83.2 | 4.8 | 1.9 | 6.7 | 1.2 | 2.7 | 2.2 | 2.6 | 6.9 | 0.6 | 112.8
| 2031 |  | 83.4 | 5.1 | 2.2 | 7.6 | 1.4 | 3.1 | 3.2 | 2.6 | 7.8 | 0.8 | 117.3
| 2032 |  | 83.6 | 5.4 | 2.5 | 8.6 | 1.7 | 3.5 | 4.1 | 2.6 | 8.7 | 1.1 | 121.8
| 2033 |  | 83.7 | 5.6 | 2.9 | 9.6 | 2.2 | 3.9 | 4.8 | 2.6 | 9.4 | 1.2 | 125.9
| 2034 |  | 83.8 | 5.9 | 3.2 | 10.6 | 2.5 | 4.4 | 5.2 | 2.6 | 9.9 | 1.3 | 129.4
| 2035 |  | 83.6 | 6.1 | 3.6 | 11.7 | 2.9 | 5 | 5.7 | 2.6 | 10.4 | 1.4 | 132.9
*Note that Power-to-heat & electrolysis are a result from the market dispatch
** Net-other industry contains both new industrial facilities (+) as wel as old processes being replaced (-) and could be negative
2.1.1. Electrification of the transport sector
Passenger cars (BEV = Battery Electric Vehicle; PHEV = Plug-In Hybrid Electric Vehicle)
| Unit | Value
Usage - company | km/year | 22750.4363
Usage - private | km/year | 12350
Consumption - BEV | kWh/100km | 18
Consumption - PHEV company | kWh/100km | 2
Consumption - PHEV private | kWh/100km | 8.5
Sales - company | thousand units/y | 235
Sales - private | thousand units/y | 180
|  |  | Company |  | Private |  |  | Total Units (BEV + PHEV)
Million units | Year | Data at end of year | BEV | PHEV | BEV | PHEV | % of stock
| 2021 |  | 0.05 | 0.11 | 0 | 0.01 | 2.9% | 0.17
| 2022 |  | 0.08 | 0.16 | 0.01 | 0.02 | 4.6% | 0.27
| 2023 |  | 0.13 | 0.23 | 0.02 | 0.04 | 7.1% | 0.42
| 2024 |  | 0.2 | 0.3 | 0.03 | 0.06 | 10.5% | 0.59
| 2025 |  | 0.34 | 0.35 | 0.06 | 0.08 | 14.8% | 0.83
| 2026 |  | 0.54 | 0.34 | 0.11 | 0.1 | 19.5% | 1.09
| 2027 |  | 0.72 | 0.31 | 0.18 | 0.12 | 23.8% | 1.33
| 2028 |  | 0.89 | 0.26 | 0.28 | 0.14 | 28.2% | 1.57
| 2029 |  | 1.02 | 0.21 | 0.4 | 0.14 | 31.8% | 1.77
| 2030 |  | 1.08 | 0.15 | 0.53 | 0.14 | 34.3% | 1.9
| 2031 |  | 1.13 | 0.11 | 0.66 | 0.14 | 36.9% | 2.04
| 2032 |  | 1.16 | 0.07 | 0.81 | 0.14 | 39.7% | 2.18
| 2033 |  | 1.19 | 0.04 | 0.96 | 0.13 | 42.6% | 2.32
| 2034 |  | 1.22 | 0.02 | 1.12 | 0.13 | 45.7% | 2.49
| 2035 |  | 1.24 | 0 | 1.28 | 0.12 | 48.7% | 2.64
Light Duty Vehicle freight (Vans)
| Unit | Value
Usage | km/year | 16 300
Efficiency - BEV | kWh/100km | 30
Efficiency - PHEV | kWh/100km | 15
Sales | thousand units/year | 60
Thousands units | Year | Data at end of year | BEV | PHEV | % of stock | Total Units (BEV + PHEV)
| 2021 |  | 3 | 1 | 0% | 4
| 2022 |  | 6 | 2 | 0.8% | 8
| 2023 |  | 11 | 4 | 1.5% | 15
| 2024 |  | 18 | 7 | 2.4% | 25
| 2025 |  | 28 | 10 | 3.7% | 38
| 2026 |  | 43 | 15 | 5.6% | 58
| 2027 |  | 63 | 19 | 8.1% | 82
| 2028 |  | 90 | 24 | 11.2% | 114
| 2029 |  | 123 | 28 | 14.9% | 151
| 2030 |  | 161 | 33 | 20.9% | 194
| 2031 |  | 202 | 36 | 23.5% | 238
| 2032 |  | 244 | 38 | 27.9% | 282
| 2033 |  | 287 | 38 | 32.2% | 325
| 2034 |  | 329 | 38 | 36.3% | 367
| 2035 |  | 372 | 35 | 42.1% | 407
Heavy Duty Vehicle freight (Trucks)
| Unit | Value
Usage | km/year | 55 250
Efficiency | kWh/100km | 120
Sales | thousand units/year | 8
thousands units | Year |  |  |  | % of stock | Total Units (BEV)
| 2021 |  |  |  | 0% | 0.018
| 2022 |  |  |  | 0% | 0.031919
| 2023 |  |  |  | 0% | 0.053835
| 2024 |  |  |  | 0.1% | 0.08942
| 2025 |  |  |  | 0.1% | 0.14729
| 2026 |  |  |  | 0.2% | 0.24347
| 2027 |  |  |  | 0.3% | 0.40113
| 2028 |  |  |  | 0.5% | 0.79051
| 2029 |  |  |  | 1.5% | 2.1197
| 2030 |  |  |  | 3.1% | 4.4658
| 2031 |  |  |  | 5.2% | 7.4344
| 2032 |  |  |  | 7.8% | 11.0217
| 2033 |  |  |  | 10.7% | 15.2145
| 2034 |  |  |  | 14.1% | 19.9586
| 2035 |  |  |  | 17.9% | 25.1951
Busses
| Unit | Value
Usage (km/year) | km/year | 45 000
Efficiency (kWh/100km) | kWh/100km | 124
thousands units | Year |  |  |  | % of stock | Total Units (BEV)
| 2021 |  |  |  | 2.9% | 0.47
| 2022 |  |  |  | 5.6% | 0.91
| 2023 |  |  |  | 8.3% | 1.36
| 2024 |  |  |  | 11.1% | 1.8
| 2025 |  |  |  | 13.9% | 2.24
| 2026 |  |  |  | 16.8% | 2.68
| 2027 |  |  |  | 19.7% | 3.12
| 2028 |  |  |  | 22.7% | 3.56
| 2029 |  |  |  | 25.7% | 4
| 2030 |  |  |  | 30% | 4.44
| 2031 |  |  |  | 36.7% | 5.62
| 2032 |  |  |  | 44.8% | 6.81
| 2033 |  |  |  | 53.1% | 7.99
| 2034 |  |  |  | 61.5% | 9.17
| 2035 |  |  |  | 70% | 10.36
2.1.2. Electrification of the heating sector
AA=Air-Air; AW=Air-Water; GW=Ground-Water
Residential
| Unit | Value
New buildings | thousand/y | 55
Renovation rate avg 2022-2035 | % | 1%
Average Heating demand - new build | kWh/y | 4400
Average Heating demand - renovated building | kWh/y | 8000
Heat supplied by secondary heater | % | 50%
Average Hot water demand | kWh/y | 1800
thousands units | Year |  | AA HP - primary | AW HP | GW HP | AA HP - secondary* | Total | % of stock | Primary | Hydronic
| 2021 |  | 87 | 71 | 21 | 330 | 509 | 8.4% | 179 | 92
| 2022 |  | 111 | 92 | 27 | 419 | 649 | 10.5% | 230 | 119
| 2023 |  | 115 | 114 | 32 | 428 | 689 | 11.1% | 261 | 146
| 2024 |  | 121 | 144 | 39 | 439 | 743 | 11.8% | 304 | 183
| 2025 |  | 128 | 188 | 49 | 450 | 815 | 12.9% | 365 | 237
| 2026 |  | 135 | 234 | 60 | 463 | 892 | 14.1% | 429 | 294
| 2027 |  | 144 | 283 | 71 | 478 | 976 | 15.3% | 498 | 354
| 2028 |  | 153 | 333 | 82 | 493 | 1061 | 16.5% | 568 | 415
| 2029 |  | 164 | 385 | 93 | 510 | 1152 | 17.8% | 642 | 478
| 2030 |  | 175 | 439 | 105 | 528 | 1247 | 19.2% | 719 | 544
| 2031 |  | 188 | 496 | 117 | 548 | 1349 | 20.6% | 801 | 613
| 2032 |  | 201 | 554 | 129 | 569 | 1453 | 22.1% | 884 | 683
| 2033 |  | 216 | 615 | 141 | 592 | 1564 | 23.6% | 972 | 756
| 2034 |  | 232 | 679 | 154 | 616 | 1681 | 25.2% | 1065 | 833
| 2035 |  | 248 | 744 | 167 | 641 | 1800 | 26.9% | 1159 | 911
note that HP reporting is often done only for hydronic types
* Included in this category are Air-Air reversible heat pumps which have seen a sharp increase in recent years. These units are typically installed as an AC (cooling) unit but also have the capability to deliver heat, albeit in general limited to a part of the building and/or as a secondary form of heating.
After consultation with ATTB, FRIXIS and contacts within the heat pump sector, these A-A (reversible) units were assumed for 80% in the hybrid category as they will have different characteristics when it comes to yearly and hourly electricity demand
Tertiary
| Unit | Value
New buildings | thousand/y | 5.8
Renovation rate avg 2022-2035 | % | 1%
Average Heating demand - new build | kWh/y | 17000
Average Heating demand - renovated building | kWh/y | 25500
Average Hot water demand | kWh/y | 3600
thousands units | Year |  | AA HP | AW HP | GW HP | AA HP (secondary)* | Total | % of stock | Primary | Hydronic
| 2021 |  | 6 | 2 | 1 | 22 | 31 | 3.9% | 9 | 3
| 2022 |  | 7 | 3 | 1 | 28 | 39 | 4.9% | 11 | 4
| 2023 |  | 8 | 7 | 2 | 30 | 47 | 6.1% | 17 | 9
| 2024 |  | 9 | 13 | 3 | 33 | 58 | 7.5% | 25 | 16
| 2025 |  | 10 | 19 | 5 | 36 | 70 | 9% | 34 | 24
| 2026 |  | 11 | 26 | 6 | 40 | 83 | 10.7% | 43 | 32
| 2027 |  | 12 | 33 | 8 | 45 | 98 | 12.6% | 53 | 41
| 2028 |  | 14 | 41 | 9 | 50 | 114 | 14.7% | 64 | 50
| 2029 |  | 16 | 50 | 11 | 55 | 132 | 17% | 77 | 61
| 2030 |  | 19 | 58 | 12 | 59 | 148 | 19.2% | 89 | 70
| 2031 |  | 20 | 67 | 14 | 64 | 165 | 21.4% | 101 | 81
| 2032 |  | 22 | 76 | 16 | 68 | 182 | 23.7% | 114 | 92
| 2033 |  | 24 | 84 | 18 | 73 | 199 | 26% | 126 | 102
| 2034 |  | 26 | 94 | 20 | 76 | 216 | 28.3% | 140 | 114
| 2035 |  | 28 | 103 | 22 | 80 | 233 | 30.7% | 153 | 125
note that HP reporting is often done only for hydronic types
2.1.3. Additional electrification in industry & data centers
This concerns new electrificaiton on top of the evolution of exisiting usages (2022)
Additional electrification in industry
TWh | Year | Additional new demand compared to 2022 | Power-to-Heat* | CCS | DRI-EAF | Other (new)** | Data centers | Electrolysis*
2022
| 2023 |  | 0.28 | 0 | 0 | 0.1 | 0.13 | 0
| 2024 |  | 0.4 | 0 | 0 | 0.2 | 0.69 | 0
| 2025 |  | 1 | 0.37 | 0 | 0.6 | 0.78 | 0.02
| 2026 |  | 1.7 | 0.7 | 2.59 | 0.8 | 1.26 | 0.08
| 2027 |  | 2.66 | 1.08 | 2.59 | 1.1 | 1.74 | 0.14
| 2028 |  | 3.86 | 2.11 | 2.59 | 1.4 | 2.05 | 0.22
| 2029 |  | 5.32 | 2.14 | 2.59 | 1.9 | 2.36 | 0.39
| 2030 |  | 6.85 | 2.24 | 2.59 | 2.3 | 2.66 | 0.6
| 2031 |  | 7.78 | 3.23 | 2.59 | 2.6 | 3.09 | 0.83
| 2032 |  | 8.66 | 4.13 | 2.59 | 3 | 3.52 | 1.09
| 2033 |  | 9.4 | 4.75 | 2.59 | 3.5 | 3.94 | 1.2
| 2034 |  | 9.89 | 5.18 | 2.59 | 3.8 | 4.37 | 1.29
| 2035 |  | 10.39 | 5.67 | 2.59 | 4.2 | 5 | 1.38
*Note that Power-to-heat & electrolysis are a result from the market dispatch
** Note that this figure only shows the increase due to new processes. As some of these also replace old process, the net increase is more limited as can be seen 'other (new)' is not the same as 'net other' in section 2.1 as here it only shows the 'increase'

## 3.1 Storage
3.1 Pumped-storage, large scale storage and small scale storage
This section concerns pumped-storage, large scale batteries and small scale batteries assumptions. For more information on the methodology and assumptions, please refer to online published study report.
3.1.1 Pumped-storage
Turbining capacity at the end of the mentioned year [MW]
|  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Turbining capacity | Total capacity | 1224 | 1224 | 1251 | 1278 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305 | 1305
|  | Coo 1-6 | 1080 | 1080 | 1107 | 1134 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161 | 1161
|  | Platte Taille 1-4 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
Reservoir volume at the end of the mentioned year [MWh]
|  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Reservoir volume | Available storage for economic dispatch | 5413 | 5413 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800 | 5800
|  | Storage reservoir | 5913 | 5913 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300 | 6300
|  | Storage reservoir derating (black-start services) | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500 | 500
3.1.2. Large scale batteries
Capacity and volume of large scale storage at the end of the mentioned year [MW] or [MWh]
|  |  |  | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Total potential capacity [MW] |  |  | 102 | 189 | 377 | 953 | 1517 | 2118 | 2195 | 2271 | 2471 | 2671 | 2871 | 3071 | 3271
| Capacity [MW] | Exisiting capacity |  | 102 | 152 | 152 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 327
|  | Additional potential if economically viable |  | 0 | 37 | 225 | 626 | 1190 | 1791 | 1868 | 1944 | 2144 | 2344 | 2544 | 2744 | 2944
| Total potential volume [MWh] |  |  | 205.8944 | 553.832 | 1305.832 | 3608.9274 | 5864.9274 | 8268.9274 | 8576.9274 | 8880.9274 | 9680.9274 | 10480.9274 | 11280.9274 | 12080.9274 | 12880.9274
| Volume [MWh] | Existing volume |  | 205.8944 | 405.832 | 405.832 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274 | 1104.9274
| Reservoir volume [MWh] | Additional potential if economically viable |  | 0 | 148 | 900 | 2504 | 4760 | 7164 | 7472 | 7776 | 8576 | 9376 | 10176 | 10976 | 11776
3.1.3. Small scale home batteries
Capacity and volume of storage at the end of the mentioned year[MW] or [MWh]
|  |  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Capacity [MW] |  | 90 | 282.25 | 345.45 | 363.87 | 384.05 | 405.99 | 429.69 | 455.15 | 482.37 | 511.35 | 542.09 | 574.59 | 608.85 | 644.87
| Total potential volume [MWh] |  | 180 | 564.5 | 690.9 | 727.74 | 768.1 | 811.98 | 859.38 | 910.3 | 964.74 | 1022.7 | 1084.18 | 1149.18 | 1217.7 | 1289.74
| Percentage assumed out-of-market |  | - | - | 100% | 70% | 50% | 40% | 30% | 20% | 10% | 0% | 0% | 0% | 0% | 0%
| Percentage assumed in-the-market |  | - | - | 0 | 30% | 50% | 60% | 70% | 80% | 90% | 100% | 100% | 100% | 100% | 100%

## 3.2. DSR industry
3.2. Demand-Side Response in industry
In this section, demand-side response in industry is detailed. For more information on the methodology and assumptions, please refer to online published study report.
Demand Side Response volume per year
Potential capacity at the end of the mentioned year [MW]
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Total potential shedding capacity* | 1664 | 1798 | 1948 | 2098 | 2248 | 2398 | 2548 | 2698 | 2848 | 2998 | 3148 | 3298 | 3448 | 3598
Market Response (DSR from existing usages) | 1664 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798
New potential submitted to EVA - 25€/kW | 0 | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New potential submitted to EVA - 50€/kW | 0 | 0 | 0 | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New potential submitted to EVA - 75€/kW | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 300 | 300 | 300 | 300 | 300 | 300
New potential submitted to EVA - 100€/kW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 300 | 450 | 600 | 750 | 900
Existing Market Response - Details in shedding capacity | 1664 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798 | 1798
Max use of 1 hour | 120 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
Max use of 2 hours | 419 | 453 | 453 | 453 | 453 | 453 | 453 | 453 | 453 | 453 | 453 | 453 | 453 | 453
Max use of 4 hours* | 587 | 634 | 634 | 634 | 634 | 634 | 634 | 634 | 634 | 634 | 634 | 634 | 634 | 634
Max use of 8 hours | 359 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388 | 388
No limit | 179 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
* The volume for ancillary services is included in the "max use of 4 hours" category
Potential capacity at the end of the mentioned year [MW]
| 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
Additional DSR from industry electrification (shedding capacity) | 0 | 0 | 68.4589 | 117.4067 | 435.7283 | 750.6679 | 992.9464 | 1203.6662 | 1301.1873 | 1426.8813 | 1550.2795 | 1673.6277 | 1815.0426 | 1909.9272
P2H - HP | 0 | 0 | 16.4568 | 30.5844 | 64.3278 | 103.363 | 154.0903 | 226.9364 | 324.2427 | 421.1241 | 479.7662 | 526.1037 | 569.3139 | 605.8158
P2H - eBoiler | 0 | 0 | 44.5021 | 47.3223 | 326.9004 | 353.2453 | 517.2965 | 637.6701 | 620.3849 | 631.6975 | 672.0889 | 724.7349 | 798.5749 | 832.593
DRI-EAF (Steel) | 0 | 0 | 0 | 0 | 0 | 222.0597 | 222.0597 | 222.0597 | 222.0597 | 222.0597 | 222.0597 | 222.0597 | 222.0597 | 222.0597
CCS | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Data centers | 0 | 0 | 7.5 | 39.5 | 44.5 | 72 | 99.5 | 117 | 134.5 | 152 | 176.3647 | 200.7294 | 225.0941 | 249.4588

## 3.3. DSR end-user
3.3. Demand-Side Response from residential and tertiary
This section concerns assumptions on demand-side response from residential and tertiary. For more information on the methodology and assumptions, please refer to the online published study report.
2. Flexibility options & forecasts
DISCLAIMERS: - This represents a best estimate based on current known policies. Other policies could improve the flexibility available (Other tariffs, market arrangements, etc…) - The numbers represent a maximum achievable penetration (with current known policies and partial rollout of an adequate market mechanism). - Categories are not exclusive. A vehicle able to do V2M, could in theory be able to do V1H, or V2H.
Maximum achievable % for each charging type
| Electric Vehicles - Residential | [6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Natural charging - V0 | [5 empty] | 76% | 70% | 65% | 57% | 51% | 44% | 36% | 30% | 25% | 19% | 14% | 8%
|  | Delayed charging - V1H | [5 empty] | 24% | 25% | 28% | 33% | 37% | 40% | 43% | 45% | 46% | 47% | 48% | 49%
|  | Smart charging - V1M | [5 empty] | 0% | 5% | 7% | 10% | 12% | 15% | 18% | 21% | 23% | 26% | 29% | 33%
|  | Vehicle-to-home - V2H | [5 empty] | 0% | 0% | 0% | 0% | 0% | 1% | 2% | 3% | 4% | 5% | 6% | 6%
|  | Vehicle-to-market - V2M | [5 empty] | 0% | 0% | 0% | 0% | 0% | 0% | 1% | 1% | 2% | 3% | 3% | 4%
| Heat Pumps - Residential | [6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Natural profile - HP0 | [5 empty] | 92% | 83% | 82% | 78% | 74% | 69% | 64% | 59% | 54% | 48% | 43% | 36%
|  | Pre-heating load - HP1H | [5 empty] | 8% | 13% | 14% | 16% | 20% | 23% | 27% | 31% | 35% | 39% | 43% | 48%
|  | Smart heating - HP1M | [5 empty] | 0% | 4% | 4% | 5% | 6% | 8% | 9% | 10% | 11% | 13% | 14% | 16%
| Batteries - Residential | [6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
|  | Natural operation - B2H | [5 empty] | 100% | 70% | 50% | 40% | 30% | 20% | 10% | 0% | 0% | 0% | 0% | 0%
|  | Market-dispatched - B2M | [5 empty] | 0% | 30% | 50% | 60% | 70% | 80% | 90% | 100% | 100% | 100% | 100% | 100%
3. Flex profiles (average winter) with assumptions
DISCLAIMERS: - HP & EV profiles displayed are for residential - HP profiles are based on an average winter weekday as these are the most representative for adequacy. Week-end & summer profile would be different.
[kW]
| Electric Vehicles |  | 0:00 | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 19:00 | 20:00 | 21:00 | 22:00 | 23:00
|  | Natural charging - V0 | 4.1% | 2.7% | 1.6% | 0.9% | 0.6% | 0.6% | 0.7% | 1.3% | 2.2% | 2.6% | 2.6% | 2.8% | 3% | 3% | 3.1% | 3.8% | 5.3% | 7.6% | 9.8% | 10.4% | 9.5% | 8.3% | 7.6% | 6.1%
|  | Delayed charging - V1H | 9.3% | 10.7% | 11.1% | 10.5% | 7.9% | 5.2% | 3.4% | 2.3% | 1.7% | 1.1% | 1.1% | 1.2% | 1.4% | 1.4% | 1.5% | 1.8% | 2.3% | 2.6% | 3% | 3.4% | 3.7% | 4.2% | 4.5% | 5.2%
|  | Smart charging - V1M | The V1M varies each year and each day based on energy and power constraints, see the report for more details (Section 3.3.3 and Appendix D)
|  | Vehicle-to-home - V2H | 21.7% | 33.9% | 38.9% | 37.2% | 28.4% | 16.7% | 9.3% | 1.6% | 1.2% | 1% | 1.1% | 1.2% | 1.3% | 1.4% | 1.4% | 1.8% | -4.4% | -9.5% | -12.2% | -12.9% | -13.2% | -11.8% | -9.4% | -4.7%
|  | Vehicle-to-market - V2M | The V2M varies each year and each day based on energy and power constraints, see the report for more details (Section 3.3.3 and Appendix D)
ASHP & GSHP - residential profile
|  | Natural load - HP0 | 2.1% | 2.3% | 2.6% | 3.1% | 3.7% | 4.7% | 5.7% | 5.9% | 5.1% | 4% | 3.5% | 3.4% | 3.5% | 3.6% | 3.9% | 4.7% | 5.5% | 5.8% | 5.7% | 5.6% | 5.3% | 4.5% | 3.4% | 2.4%
|  | Pre-heated load - HP1H | 2.2% | 2.5% | 2.9% | 3.5% | 4.4% | 5.4% | 5.7% | 5% | 4.3% | 4.2% | 4.6% | 4.8% | 4.9% | 4.3% | 3.8% | 4% | 4.5% | 4.9% | 5.1% | 5% | 4.5% | 3.9% | 3.3% | 2.6%
|  | Smart heating - HP1M | The HP1M varies each year and each day based on energy and power constraints, see the report for more details (Section 3.3.4 & Appendix D)

## 3.4. Electrolysers
3.4. Electrolysers
This section concerns assumptions on additional electrolysers. For more information on the methodology and assumptions, please refer to the online published study report.
Installed capacity at the end of the mentioned year [MW]
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034
| Electrolysers | 0 | 0 | 0 | 0 | 75 | 150 | 224 | 298 | 373 | 447 | 521 | 595 | 669 | 743

## 4.1. Fuel and CO2 prices
4.1. Fuel and CO2 prices
This section concerns assumptions on fuel and CO2 prices. For more information on the methodology and assumptions, please refer to the online published study report.
Fuel and CO2 prices per year
Prices are displayed in the table corresponding the calender year, as published in the relevant sources.
The methodology applied to establish is the following: - Average for the year 2022 has been established based on historical data (see the relevant source) - For Natural Gas, Coal and Oil, forward prices from contracts were taken on 28/02/2022 (see the relevant source) - For the rest of the data, an interpolation was carried out between the last computed price and the prices of the WEO2022 in 2030. The "Announced Pledges" scenarop was used. - After 2030, a interpolation is carried out between the WEO2022 prices' available target years. - WEO22 prices being expressed in EUR21, an inflation rate of 9.6% was applied as reported by the Federaal Planbureau (https://www.plan.be/uploaded/documents/202302231209220.FOR_MIDTERM2328_12798_N.pdf) Note a split has been done between UK and the rest of the EU for Natural Gas & CO2.
Price in [€2022] | Years | [12 empty] | Sources |  |  | AREA | Comments
| 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Historical average | Forward | Long term |  | Historical average (2022) | Forward (up to 2025) | Long term (until 2035)
Gas TTF [€/MWh] | 123.9 | 49.9 | 59 | 48 | 35.5 | 31 | 31 | 28 | 24.9 | 24.7 | 24.4 | 24.2 | 23.9 | BNEF | Futures (eex.com) | World Energy Outlook 2022 – Analysis - IEA | EU except UK |  | Consulted on 28/02/2022, use of the average of February | Announced Pledges scenario taken from WEO 2022
Gas NBP [€/MWh] | 82.7 | 54.6 | 67.5 | 58.6 | 49 | 42.9 | 36.9 | 30.9 | 24.9 | 24.7 | 24.4 | 24.2 | 23.9 | BNEF | Futures (eex.com) | World Energy Outlook 2022 – Analysis - IEA | UK |  | Consulted on 28/02/2022, use of the average of February | Announced Pledges scenario taken from WEO 2022
Coal ARA [€/MWh] | 38.6257 | 20 | 20.7 | 19.6 | 18.6 | 17.7 | 14.6 | 11.4 | 8.2 | 8.2 | 8.1 | 8.1 | 8 | BNEF | Coal (API2) CIF ARA (ARGUS-McCloskey) Futures Quotes - CME Group | World Energy Outlook 2022 – Analysis - IEA | EU |  | Consulted on 28/02/2022, use of the average of February | Announced Pledges scenario taken from WEO 2022
Oil [€/MWh] | 54.9 | 43.5 | 41.1 | 38.7 | 36.7 | 35 | 33.5 | 34.9 | 36.3 | 36.2 | 36.1 | 36 | 35.9 | Brent crude oil - 2023 Data - 1970-2022 Historical - 2024 Forecast - Price - Quote (tradingeconomics.com) | Crude Oil Futures Quotes - CME Group | World Energy Outlook 2022 – Analysis - IEA | EU |  | Consulted on 28/02/2022 | Announced Pledges scenario taken from WEO 2022
CO2 EUA [€/tCO2] | 81.2 | 94.9 | 98.5 | 103.8 | 107 | 111.4 | 115.9 | 120.3 | 124.7 | 128.4 | 132.1 | 135.8 | 139.5 | BNEF | Futures (eex.com) | World Energy Outlook 2022 – Analysis - IEA | EU except UK |  | Consulted on 28/02/2022, use of the average of February | Announced Pledges scenario taken from WEO 2022
CO2 UKA [€/tCO2] | 90.4 | 96.4 | 102.3 | 108.3 | 111.6 | 114.9 | 118.2 | 121.5 | 124.7 | 128.4 | 132.1 | 135.8 | 139.5 | Carbon pricing ¦ Ember (ember-climate.org) |  | World Energy Outlook 2022 – Analysis - IEA | UK |  |  | Announced Pledges scenario taken from WEO 2022
Legend: |  | Methodology:
Historical average
Forward prices |  |  | Historical average (for the year 2022)
WEO prices
Interpolation to WEO prices
Prices defined by forward contracts, as displayed on relevant source, consulted in January 2023 (on 28/02/2023, use of the average of February)
Interpolation between last forward price known & long-term price defined in WEO2022 for 2030 and 2050.
2
1
2
3
3
1
2
3
1
2
3
1
3
2
3

## 4.2 Investment costs
4.2. Investment costs
This section concerns assumptions on investment costs. For more information on the methodology and assumptions, please refer to the online published study report.
All prices are assumed to be in €2022 end of the year
A large amount of sources has been consulted (see below in 'Sources') and feedback from the public consultation are integrated.
For some values, the data taken into account in the AdeqFlex'21 study are taken as basis. Latest inflation figures are taken into account since the publication of previous AdeqFlex'21 which included costs expressed in €2019:
| 2019 | 2020 | 2021 | 2022* | Source
General Inflation | 0.76% | 0.41% | 5.71% | 9.08% | Historische inflatie België – historische CPI inflatie België (inflation.eu) | *10/2021-10/2022
Industrial PPI | 1.111% | -2.854% | 19.85% | 13.94% | Output price index (industry) ¦ Statbel (fgov.be) | *01/2022-08/2022
Labour cost (Electricity, gas, steam and air conditioning supply (D) ) | 1.623% | 1.942% | 3.079% | 4.082% | Labour Cost Index ¦ Statbel (fgov.be) | *01/2022-07/2022
The industry wide real WACC proposed for this study is 4.7%. In addition, a technology specific hurdle premium was added to obtain the hurdle rate per technology.
All figures in EUR 2022
Technologies part of the structural block |  | Applies to | CAPEX [€/kW] |  |  | FOM (including major overhauls) [€/kW/y] | Construction period | Investment economic lifetime [years] | Hurdle rate in EOM (WACC + premium) | Hurdle rate in CRM (WACC + premium) | Main Sources (see also dedicated sections in the present study)
|  |  | 2022-2025 | 2026-2030 | 2031-2035 | 2022-2035 | 2022-2035 | 2022-2035 | 2022-2035 | 2022-2035 | Source CAPEX | Source FOM
Existing (assumed no extension costs) | CCGT | Existing units <25 years | - |  |  | 40 | - | - | 7.7% | 6.6% |  | Afry 2022
| OCGT |  | - | - | - | 25 | - | - | 8.2% | 7.6% |  | Afry 2022
| CHP | All existing capacity | - | - | - | 70 | - | - | 7.7% | 6.6% |  | AdeqFlex'21 + inflation
| Turbojets | All existing capacity | - | - | - | 35 | - | - | 8.2% | 5.3% |  | Afry 2022
| Demand Response | All existing capacity in 2020 | - | - | - | 12 | - | - | 8.2-8.9% | 5.9-6.7% |  | AdeqFlex'21 + inflation | *depending on activation costs
| Pumped Storage | All existing capacity | - | - | - | 32 | - | - | 6.9% | 5% |  | Afry 2022
Existing (assuming extension costs needed) | CCGT | Existing units >25 years | 120 |  |  | 37 | 0 | 15 | 8.7% | 6.8% | AdeqFlex'21 X (Weighted avg Labour + Industrial PPI) (~Afry 2022) | Afry 2022
| OCGT |  | 100 |  |  | 50 | 0 | 15 | 9.7% | 7.2%
New | CCGT | >800 MW | 700 |  |  | 30 | 3 | 20 | 9.2% | 6.9% | AdeqFlex'21 X (Weighted avg Labour + Industrial PPI) (~Afry 2022) and feedfback public consultation | Afry 2022
|  | 400 < 800 MW | 850 |  |  | 35 | 3 | 20 | 9.2% | 6.9%
|  | < 400 MW | 1050 |  |  | 35 | 3 | 20 | 9.2% | 6.9%
|  | H2 fueled >800W | - |  | 800 | 35 | 3 | 20 | 9.2% | 6.9% | Bloomberg | Bloomberg
| OCGT | >100 MW | 550 |  |  | 25 | 2 | 20 | 10.7% | 8% | AdeqFlex'21 X (Weighted avg Labour + Industrial PPI) (~Afry 2022) and feedfback public consultation | Afry 2022
|  | <100 MW | 1000 |  |  | 25 | 2 | 20 | 10.7% | 8% |  | Afry 2022
|  | H2 fueled >100W | - |  | 700 | 30 | 2 | 20 | 10.7% | 8% | Bloomberg | Bloomberg
| CHP | New capacity < 100 MW | 1000 |  |  | 70 | 2 | 20 | 9.2% | 6.9% | AdeqFlex'21 X (Weighted avg Labour + Industrial PPI) (~Afry 2022) | Several Sources + inflation
| Demand response | New capacity 0 < 300 MW | All costs included in the FOM |  |  | 25 | 0 | - | 8.2-8.9% | 5.9-6.7% | AdeqFlex'21 X (Weighted avg Labour + Industrial PPI) (~Afry 2022) | DSM sources (see dedicated section) | *depending on activation costs
|  | New capacity 300 < 600 MW |  |  |  | 50 | 0 | - | 8.2-8.9% | 5.9-6.7% |  |  | *depending on activation costs
|  | New capacity 600 < 900 MW |  |  |  | 75 | 0 | - | 8.2-8.9% | 5.9-6.7% |  |  | *depending on activation costs
|  | New capacity 900 < 1200 MW |  |  |  | 100 | 0 | - | 8.2-8.9% | 5.9-6.7% |  |  | *depending on activation costs
| Batteries/Storage | Large scale batteries (1h) | 450 | 300 | 300 | 20 | 1 | 15 | 7.7% | 5.1% | NREL | NREL
|  | Large scale batteries (2h) | 750 | 500 | 450 | 20 | 1 | 15 | 7.7% | 5.1%
|  | Large scale batteries (4h) | 1200 | 900 | 750 | 20 | 1 | 15 | 7.7% | 5%
| Pumped Storage - new unit | New unit in Coo | 2000 |  |  | 32 | 4 | 25 | 7.7% | 5% | NREL | Afry 2022
Renewables
RES | Wind onshore | New | 1150 | 1000 | 900 | 45 | 1 | 15 | 6.9% | 6% | Indexation + benchmark with several sources incl. IRENA (2021), IEA (2021), EnergyVille (2022) | Indexation + EnergyVille
| Wind offshore | New (after 2 GW) | 2650 | 2000 | 1850 | 70 | 3 | 15 | 6.9% | 5.2%
| PV | New | 800 | 600 | 500 | 20 | 0 | 15 | 6.9% | 5.1%
| Biomass | New | 2300 | 2300 | 2300 | 95 | 3 | 20 | 7.7% | 5% | AdeqFlex'21 + inflation | AdeqFlex'21 + inflation
Batteries: sources
https://www.elia.be/en/public-consultation/20220506_public-consultation-on-crm
Cost Projections for Utility-Scale Battery Storage: 2021 Update (nrel.gov)
DSM: sources
https://www.ademe.fr/sites/default/files/assets/documents/effacement-consommation-electrique-france_2017-synthese.pdf
https://www.cre.fr/content/download/21610/275050
New Sources used
AFRY - peer review study presented to the TF CRM on 13/10/2022
PATHS2050 ¦ Energy outlook (energyville.be)
Lazard.com ¦ Levelized Cost Of Energy, Levelized Cost Of Storage, and Levelized Cost Of Hydrogen
World Energy Outlook 2022 (windows.net)
Renewable power generation costs in 2021 (irena.org)
EN2021_Fraunhofer-ISE_LCOE_Renewable_Energy_Technologies.pdf
Sources used in Previous AdeqFlex (2021) & indexed for comparison
Bloomberg (not public)
https://www.elia.be/-/media/project/elia/elia-site/public-consultations/2020/20200505_fichtner-report-cost-of-capacity-crm_en.pdf
https://setis.ec.europa.eu/system/files/ETRI_2014.pdf
https://ec.europa.eu/energy/sites/ener/files/documents/2018_06_27_technology_pathways_-_finalreportmain2.pdf
https://economie.fgov.be/sites/default/files/Files/Energy/Seuils-investissements-CREG-Feedback-PwC-20200207.pdf
https://www.rtbf.be/info/regions/liege/detail_un-troisieme-bassin-a-coo-ou-le-retour-d-une-arlesienne?id=9383349
https://www.semcommittee.com/sites/semc/files/media-files/SEM-18-156a%20Poyry%20Report%20-%20Cost%20of%20New%20Entrant%20Peaking%20Plant%20and%20Combined%20Cycle%20Plant%20in%20I-SEM.pdf
https://www.energyville.be/sites/energyville/files/downloads/2020/20200918_fullpresentation_0.pdf
Cost of life-time extension of Seraing (Trends Tendance article 27/08/14) with inflation
Note on E30: Author: to check after meeting Siemens

## 4.3. Outages
4.3. Outages
This section concerns assumptions on outages. For more information on the methodology and assumptions, please refer to the online published study report.
4.3.1. Forced outage rates
Category | Number of FO per year | Average FO rate [%] | Average duration of FO rate [hours]
Nuclear | 1.3* | 20.5%** | 199 hours* [around 8 days]
CCGT | 9.4 | 5.5% | 110 hours [ around 5 days]
OCGT | 9.2 | 8.2% | 221 hours [around 9 days]
TJ | 3.2 | 9.8% | 130 hours [around5 days]
CHP, waste, biomass | 2.9 | 6.4% | 111 hours [around 5 days]
Pumped Storage | 5.8 | 2.9% | 46 hours [around 2 day]
Batteries | / | 2.0%*** | /
DC links | 1.9 | 6.7% | 158 hours [around 7 days]
* Only considering technical forced outages.
** Also considering long-lasting forced outages
*** Regarding batteries, the forced outage rate is considered in the models by applying a derating factor on the installed capacity
4.3.2. Planned outages
The latest public information (REMIT) regarding the planned outages was used
For years were no data are available in REMIT, the data from ENTSO-E was used : https://www.entsoe.eu/outlooks/midterm/

## 4.4. Short-term flex. charact.
4.4. Short-term flexibility characteristics
This section concerns assumptions on short-term flexibility. For more information on the methodology and assumptions, please refer to the online published study report.
| Parameters | [8 empty] | Maximum upward flexibility |  |  | Maximim downward flexibility |  |  | Energy Limit | Clarification, justifications and remarks
Parameter | Minimum up time | Minimum down time | Hot start up time | Warm start up time | Cold start up time | Transition time from "hot" to "warm" | Transition time from "warm" to "cold" | Min Stable power | Ramp Rate | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit | Ramping flexibility limit | Fast flexibility limit | Slow flexibility limit
Definition | Duration that a unit needs to remain in "on" status after the start of an activation | Duration that a unit needs to remain in "off" status after the end of an activation | Duration between the activation signal and attaining minimum stable power in "hot", "warm" or "cold" conditions |  |  | Duration that a unit goes from "hot" to "warm" status after the end of an activation | Duration that a unit goes from "warm" to "cold" status after the end of an activation | Minimum power output level when in "on" status | Minimum power variation in a time period | Maximum share of the installed capacity which can participate in the categories upward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | Maximum share of the installed capacity which can participate in the categories downward ramping, fast and slow flex (without accounting other constraints, e.g. ramp rate) |  |  | expressed in number of hours during which the plant can product at its maximum capacity
Unit | hours | hours | hours | hours | hours | hours | hours | % Pmax | %Pmax/min | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | %Pmax | hours
Nuclear
Interconnections (AC & DC) | [9 empty] | ATC import -Pnom import |  |  | ATC export - Pnom export |  |  |  | Cross-border flexibility is constrained by the remaining import / export capacity after the day-ahead schedules. Additional constraints are implemented following :
*the availability of the cross-border energy service, particularly during high (> 300 €/MWh - reduced upward flexibility) / low price (< 0 €/MWh - reduced downward flexibility) periods
*estimations on balancing market liquidity on European balancing market platforms on aFRR and mFRR (by means of sensitivities)
*Ramping : 0 MW with sensitivity up to 75 MW, equal to 50 % aFRR needs
*Fast : 250 MW / 350 MW (= reserve sharing limits) with sensitivities equal to 50% mFRR needs
Renewable Generation
Wind offshore | [8 empty] | 100% |  |  |  | 65%Pnom | 65% Pnom | 65% Pom |  | Based on literature [1] and constrained based on day-ahead forecast errors (99th percentile of observed forecast errors).
Ramping flexibility limited to 400 MW and 925 MW of the installed offshore fleet (based on an installed capacity of 4.4 GW ) based on input stakeholders.
*This equals a share before 2028 : *18% of installed capacity ; As from 2028: *21% of installed capacity
Wind onshore (only share CIPU) | [8 empty] | 100% |  |  |  |  | 90% Pnom | 90% Pnom |  | Based on literature [1] and further constrained based on day-ahead forecast errors (99th percentile of observed forecast errors).
Solar (only share CIPU) | [8 empty] | 100% |  |  |  |  | 90% Pnom | 90% Pnom |  | Based on return on experience, and analysis of day-ahead forecast errors
Run-of-River Hydro
Biofuel (only share CIPU) | 8h | 8h | 3h | 5h | 7h | 12h | 72h | 40% | 3% |  |  |  | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [2] and CHP recent steam turbine values
CCGT
new | 2h | 2h | 1h | 1.5h | 2h | 8h | 48h | 30% | 11% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and [4]
(to be commissioned)
recent | 3h | 3h | 1.5h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
(commissioned after 2000)
old | 3h | 3h | 1.5h | 2,5h | 4h | 8h | 48h | 45% | 3% | Pmax-Pnom (0% when "off") | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
(commissioned before 2000)
OCGT
new | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 20% | 15% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on literature [3] and [4]
existing | 1h | 1h | 0.16h | 0.16h | 0.16h | 2h | 3h | 30% | 12% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off")
CHP
CHP (GAS TURBINE) | 4h | 4h | 1h | 1h | 4h | 2 h | 3 h | 50% | 10% |  |  |  | Pnom-Pmin | Pnom-Pmin | Pnom-Pmin | 8 hours | Based on literature [3] and CHP recent steam turbine values (+ [5] for energy limit) + input COGEN
CHP (CCGT) | 3h | 3h | 1h | 2h | 3h | 8h | 48h | 40% | 6% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom-Pmin | Pnom-Pmin | Pnom-Pmin |  | Based on literature [3] and CHP recent steam turbine values (+ [5] for energy limit) + input COGEN
Large-scale storage
Pumped Storage | [8 empty] | 100% | Pmax- Max(0;Pnom) (0% when "off") | Pmax - Pnom | Pmax - Pnom | Pnom-Min(0;Pmin) (0% when "off") | Pnom - Pmin | Pnom - Pmin | 4,5 hours | Aggregation of PHS-sites. Based on literature review [6; 7] and Elia's internal information *Pnom can be positive (power injections) or negative (power off-take) *Pmax is a positive value (maximum injection), Pmin is negative value (maximum offtake)
Large battery storage | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmin | Pnom - Pmin | Pnom - Pmin | 1 hours
Demand Response
All categories | [8 empty] | 100% | min (10% Pmax ; Pmax - Pnom) | min (40% Pmax ; Pmax - Pnom) | Pmax - Pnom |  |  |  | 1, 2 , 4, 8 hours - no limit | Based on E-Cube study and and Elia's estimation [9]
New technologies
1. Home batteries | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmin | Pnom - Pmin | Pnom - Pmin | 2 hours | Based on literature review [9;10;11] and DELTA-EE study [14] *For home batteries and vehicle-to-market *Pnom can be positive (power injections) or negative (power off-take) *Pmax is a positive value (maximum injection), Pmin is negative value (maximum offtake) *For heat pumps and smart vehicle charging *Energy limit equals energy which can beactivated throughout the day (not in one stretch) *Pmax / Pmin are determined by limitations related to consumer comfort
2A. Heat Pumps - Sanitary Hot Water | [8 empty] | 100% | min(50% Pmax;Pmax-Pnom) | min(70% Pmax;Pmax-Pnom) | Pmax-Pnom |  |  |  | 7 hours
2B. Heat Pumps - Space Heating | [8 empty] | 100% | min(50% Pmax;Pmax-Pnom) | min(70% Pmax;Pmax-Pnom) | Pmax-Pnom |  |  |  | 5 hours*
3A. Smart charging electric vehicle | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom |  |  |  | 8 hours*
3B. Vehicle-to-market | [8 empty] | 100% | Pmax-Pnom | Pmax-Pnom | Pmax-Pnom | Pnom - Pmin | Pnom - Pmin | Pnom - Pmin | 3 hours
Electrolyzers | [8 empty] | 100% |  | Pnom (0% when "off") | Pnom (0% when "off") |  |  |  |  | Based on literature [12]
Diesel + Turbojets | 0 h | 0.10 h | 0.05 h | 0.05 h | 0.05 h | 0 | 0 | 30% | 100% | Pmax-Pnom (0% when "off") | Pmax-Pnom (100% when "off") | Pmax-Pnom (100% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") | Pnom-Pmin (0% when "off") |  | Based on Internal Combustion Engines [13]
Terminology
Pmax | Maximum injected power of the unit (MW)
Pmax- | Maximum absorbed power of the unit (MW), i.e. negative value
Pnom | Day-Ahead Scheduled power of the unit (MW), i.e. positive or negative value
Pmin | Minimum stable power (MW)
ATCexport | Maximum available export capacity (MW)
ATCimport | Maximum available import capacity (MW)
ramping flex | Capacity which can be regulated continuously up- or downward in a timeframe of one minute
fast flex | Capacity which can be regulated up- or downward in a time frame of 15 minutes
slow flew | Capacity which can be regulated up- or downward in a time frame of 5 hours
List of references
1 | Van de vyver et al. | Comparison of wind turbine power control strategies to provide power reserves | [9 empty] | https://ieeexplore.ieee.org/abstract/document/7514034
2 | Dotzauer et al. | How to measure flexibility – Performance indicators for demand driven power generation from biogas plants | [9 empty] | https://www.sciencedirect.com/science/article/pii/S0960148118312059#sec3
3 | ENTSO-E | MAF Data | [9 empty] | https://www.entsoe.eu/Documents/SDC%20documents/MAF/MAF_2018_Dataset.xlsx
4 | Agora | Flexibility in thermal power plants, with a focus on existing coal-fired power plants | [9 empty] | https://www.agora-energiewende.de/fileadmin2/Projekte/2017/Flexibility_in_thermal_plants/115_flexibility-report-WEB.pdf
5 | Danish Energy Agency | Flexibility in the Power System - Danish and European experiences | [9 empty] | https://ens.dk/sites/ens.dk/files/Globalcooperation/flexibility_in_the_power_system_v23-lri.pdf
6 | Deloitte | Assessing the economic conditions of Belgian pumped-hydroelectric storage: comparative review of profitability drivers in Europe and evaluation of the current situation | [9 empty] | https://www.creg.be/sites/default/files/assets/Consult/2018/1718/RA1718-Annex2.7.pdf
7 | e-Storage | Potential, Economic and Environmental Value of Large-Scale Energy Storage in Europe | [9 empty] | http://www.estorage-project.eu/wp-content/uploads/2013/06/eStorage-D3.2-Value-of-storage.pdf
8 | E-Cube Strategy Consultants | Market Response study 2017 – 2nd phase report | [9 empty] | https://www.elia.be/-/media/project/elia/elia-site/electricity-market-and-system---document-library/adequacy---strategic-reserve/2018/20170712_e-cube_market-response_report_phase2.pdf
9 | Gils, H. | Assessment of the theoretical demand response potential in Europe | [9 empty] | https://www.sciencedirect.com/science/article/abs/pii/S0360544214001534
10 | Le Baut et al. | Characterization of flexibility resources and distribution networks | [9 empty] | http://smartnet-project.eu/wp-content/uploads/2017/05/D1.2_20170522_V1.1.pdf
11 | Brouwer et al. | Least-cost options for integrating intermittent renewables in low-carbon power systems | [9 empty] | https://www.sciencedirect.com/science/article/abs/pii/S0306261915012167
12 | IRENA | Green Hydrogen Cost Reduction | [9 empty] | https://www.irena.org/publications/2020/Dec/Green-hydrogen-cost-reduction
13 | Wartisla | Reciprocating engines as a source reciprocating engines as a source of flexibility in a power system | [9 empty] | https://www.cire.pl/pliki/2/2018/13___niewinski.pdf
14 | DELTA-EE | Assumptions published with the Adequacy and Flexibility Study for Belgium 2024-2034 | [9 empty] | https://www.elia.be/en/electricity-market-and-system/adequacy/adequacy-studies

## 5.1. Flow based domains
5.1. Flow-based domains
This section concerns assumptions on flow-based domains. For more information on the methodology and assumptions, please refer to the online published study report.
5.1.1. Main parameters
Market Parameters |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Comments
Flow-based perimeter |  | CORE
Bidding zones |  | As Is | [11 empty] | ACER Decision No 11-2022 on the alternative bidding zone configurations only refers to assessment by next BZR study, so no official new configuration is known at this moment
minRAM |  | See table below | [11 empty] | https://acer.europa.eu/Official_documents/Acts_of_the_Agency/Publications%20Annexes/ACER%20Report%20on%20the%20result%20of%20monitoring%20the%20MACZT%20Generic/ACER%20Report%20on%20the%20result%20of%20monitoring%20the%20MACZT%20Derogations.pdf
Treatment of external flows |  | Standard Hybrid Coupling (SHC) |  | Advanced Hybrid Coupling (AHC) - (except for Channel ICs)
External & Allocation constraints |  | No allocation constraint for Belgium from 2024 onwards* | [11 empty] | * Assumed that simultaneous 'Max Import' is systematically not higher than 9.000MW **See JAO Publication Tool for monthly statistics on the dynamic allocation constraint for Poland and External constraint of The Netherlands
Dynamic Allocation constraint for PL for all years**
External constraint on Core net position of NL (Import: 6500/Export: 6500) until 2023**
Use of PST in capacity calculation |  | For Belgium: 1/2 For other: 1/3 | [11 empty] | All get a setpoint based on the nodal flow estimation (FE). In capacity calculation only the currently known PST’s are selected (BC). In capacity allocation none participate (MC)
Use of HVDC in flow-based capacity allocation |  | Only ALEGrO
Modelling of Channel HVDC (NemoLink, IFAs, BritNed, Noth Sea Link, etc..) |  | Consideration of 'Explicit Allocation' after Brexit by means of SHC | [11 empty] | See eg section 5.1.3 “Post-Brexit trading arrangements with the United Kingdom” (page 53) of the Belgian Regulator (CREG) Monitoring Report 2021
5.1.2. MinRAM trajectories
Country |  | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Justification
Austria | CORE borders | 39.04 | 49.36 | 59.68 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2021-2025; Derogation for 2022 (related to loop flows & PST flows)
Belgium* | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | *With the application of a derogation
Netherlands | CORE borders | 47.8 | 55.2 | 62.6 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2020-2025; Derogation for 2022 (related to floop flows & redispatching)
Germany | CORE borders | 40.78 | 50.52 | 60.26 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2020-2025
France | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Slovenia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
Kroatia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Plans to adopt a action plan mid-2022; Derogation for 2022 (several reason)
Romania | CORE borders | 47.8 | 55.2 | 62.6 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2021-2025
Czechia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Derogation for 2022 (loop flows, internal flows, reliability margins)
Slovakia | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Derogation for 2022 (related to operational security)
Poland | CORE borders | 49.6 | 56.4 | 63.2 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Action plan 2020-2025; Derogation for 2022 (related to floop flows & non-coordinated transit flows); max value
Hungary | CORE borders | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | Public consultation of action plan in 2021

## 6.1. Data for other countries
6.1. Data for other countries
This section concerns assumptions on other countries. For more information on the methodology and assumptions, please refer to the online published study report.
Numbers reported correspond to the end of the mentioned year for installed capacity, and to the calendar year for the load.
Numbers above 20 are rounded.
France
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 467 | 473 | 480 | 489 | 497 | 506 | 516 | 525 | 538 | 547 | 557 | 566 | • ERAA22
| Onshore Wind | GW | 22 | 24 | 25 | 25 | 26 | 27 | 27 | 28 | 28 | 29 | 30 | 30 | • Futurs Energétiques (October 2021)
| Offshore Wind | GW | 1.5 | 1.9 | 2.2 | 2.6 | 2.9 | 3.3 | 3.6 | 4 | 6.8 | 9.6 | 12.4 | 15.2 | • Public consultation for the next “Bilan Prévisionnel” foreseen to be published after summer 2023
| Solar | GW | 19 | 21 | 24 | 29 | 34 | 40 | 43 | 47 | 51 | 55 | 59 | 63 | • Macron’s Belfort announcement from February 2022 (lower investments in onshore wind* + nuclear extension**)
| Coal | GW | 1.1 | 1.1 | 1.1 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | • Green light from the French government regarding the extension and conversion of Cordemais
| Nuclear | GW | 61 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
Germany
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 533 | 554 | 574 | 589 | 604 | 619 | 634 | 649 | 683 | 716 | 749 | 783 | • ERAA22
| Onshore Wind | GW | 63 | 69 | 77 | 84 | 92 | 99 | 107 | 115 | 121 | 127 | 134 | 140 | • Easter package (April 2022)
| Offshore Wind | GW | 9 | 9.9 | 10.8 | 11.8 | 12.7 | 14.5 | 20 | 30 | 34 | 38 | 42 | 44 | • Netzentwicklungsplan Strom 2037 - Version 2023 (March 2023 edition, data published earlier in 2022)
| Solar | GW | 77 | 88 | 108 | 128 | 150 | 172 | 194 | 215 | 234 | 252 | 271 | 290 | • Flächenentwicklungsplan 2023 für die deutsche Nordsee und Ostsee (January 2023)
| Coal | GW | 37 | 28 | 25 | 18.9 | 13.6 | 7.4 | 0 | 0 | 0 | 0 | 0 | 0
| Nuclear | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Netherlands
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 116 | 120 | 124 | 130 | 135 | 141 | 148 | 155 | 163 | 171 | 179 | 187 | • ERAA22 / Alligned with ML 2022 - Hogere Ambitie for 2030
| Onshore Wind | GW | 7.5 | 8.7 | 9.9 | 10.3 | 10.7 | 11.2 | 11.6 | 12 | 12.4 | 12.8 | 13.1 | 13.5 | • Monitoring leveringszekerheid (TenneT, 2021)
| Offshore Wind | GW | 3.9 | 6.1 | 6.1 | 6.1 | 8.1 | 12.1 | 17.5 | 24 | 25 | 26 | 27 | 28 | • Monitor Zon-PV and Wind op Land 2022 in Nederland
| Solar | GW | 24 | 29 | 34 | 37 | 40 | 43 | 46 | 49 | 52 | 55 | 58 | 61 | • Offshore government announcement (March, 2021)
| Coal* | GW | 3 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 0 | 0 | 0 | 0 | 0 | 0 | • Ontwikkelkader windenergie op zee (June 2022)
| Nuclear | GW | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0 | * Coal excluding biofuel as secondary fuel
Great Britain
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 290 | 293 | 295 | 298 | 304 | 316 | 329 | 342 | 361 | 381 | 404 | 426 | • ERAA22
| Onshore Wind | GW | 15.1 | 18 | 19.9 | 22 | 25 | 27 | 29 | 30 | 31 | 32 | 33 | 35 | • Future Energy Scenarios (July 2022)
| Offshore Wind | GW | 16.6 | 21 | 23 | 28 | 30 | 36 | 45 | 52 | 57 | 60 | 71 | 74 | • Unit-by-unit analysis for nuclear
| Solar | GW | 16.4 | 18.7 | 21 | 23 | 26 | 29 | 31 | 34 | 38 | 40 | 45 | 47 | • CRM results (published before end February 2023)
| Coal | GW | 1.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nuclear | GW | 6 | 6 | 6 | 3.6 | 6.8 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 7.6 | 7.6
Spain
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 243 | 251 | 259 | 260 | 260 | 261 | 262 | 263 | 265 | 265 | 266 | 267 | • ERAA22
| Onshore Wind | GW | 31 | 34 | 37 | 40 | 43 | 45 | 48 | 50 | 51 | 53 | 54 | 56 | • Spanish Roadmap
| Offshore Wind | GW | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 3 | 3 | 3 |  | • Hoja de Ruta para el desarrollo de la Eólica Marina y de las Energías del Mar (miteco.gob.es)
| Solar | GW | 23 | 29 | 34 | 39 | 44 | 50 | 55 | 60 | 65 | 71 | 76 | 81 |  | • Hoja de Ruta del Autoconsumo (miteco.gob.es)
| Coal | GW | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | • El Gobierno aprueba la Estrategia de Almacenamiento Energético, clave para garantizar la seguridad del suministro y precios más bajos de la energía (miteco.gob.es).
| Nuclear | GW | 7.1 | 7.1 | 7.1 | 7.1 | 6.1 | 5.1 | 3 | 2.1 | 2.1 | 2.1 | 1 | 0 |  | • Estado del acceso y conexión de la generación renovable eólica y solar fotovoltaica ¦ Red Eléctrica (ree.es)
Italy
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 321 | 325 | 329 | 332 | 335 | 342 | 350 | 355 | 360 | 364 | 369 | 373 | • ERAA22
| Onshore Wind | GW | 11.9 | 12.9 | 13.8 | 14.8 | 15.7 | 16.6 | 17.6 | 18.5 | 19.4 | 20 | 21 | 22 | • DDS2022 : «Documento di descrizione degli scenari 2022»
| Offshore Wind | GW | 1 | 2.2 | 3.2 | 4.2 | 5.3 | 6.4 | 7.4 | 8.5 | 9.6 | 10.6 | 11.7 | 12.7 | • Solar Europe 2022
| Solar | GW | 30 | 37 | 43 | 49 | 56 | 62 | 68 | 75 | 81 | 87 | 93 | 100 | • IEA Wind TCP
| Coal | GW | 1.7 | 0.5 | 0.5 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Nuclear | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Poland
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 164 | 165 | 167 | 171 | 174 | 178 | 181 | 185 | 188 | 192 | 195 | 199 | • ERAA22
| Onshore Wind | GW | 10.9 | 11.06 | 11.06 | 11.2 | 11.34 | 11.48 | 11.62 | 11.76 | 11.9 | 12.04 | 12.18 | 12.32 | • Energy Policy of Poland until 2040 (02/02/2021)
| Offshore Wind | GW | 0 | 0 | 0.6 | 3.71 | 5.93 | 5.93 | 5.93 | 6.4 | 6.9 | 7.3 | 7.8 | 8.2 | • Latest trends (solar, onshore wind) based on historical data
| Solar | GW | 14.6667 | 17.3333 | 20 | 22 | 23 | 25 | 27 | 29 | 30 | 32 | 34 | 35
| Coal | GW | 22 | 21 | 21 | 21 | 21 | 20 | 20 | 16 | 15.6 | 14.5 | 13.8 | 11.6
| Nuclear | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Denmark
| Parameter | Units | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | Sources / Infos :
| Demand | Twh | 36 | 39 | 41 | 44 | 47 | 50 | 53 | 56 | 58 | 60 | 61 | 63 | • ERAA22
| Onshore Wind | GW | 4.9 | 5.3 | 5.7 | 6.3 | 6.8 | 7.1 | 7.3 | 7.4 | 7.5 | 7.5 | 7.5 | 7.2 | • Analyseforudsætninger til Energinet (23/09/2022)
| Offshore Wind | GW | 2.7 | 2.8 | 3.1 | 4.3 | 4.3 | 5.3 | 8.3 | 13.3 | 13.3 | 16.3 | 17.3 | 20 | • Energy Agency revisits cases of planned coal plant closures (01/10/2022)
| Solar | GW | 3.5 | 5.9 | 8.2 | 10.6 | 13 | 15.4 | 17.7 | 18.6 | 19.5 | 20 | 21 | 22
| Coal | GW | 0.8 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
| Nuclear | GW | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0